## Executive Summary
Executive Summary: DISIS-2017-001-1 Restudy of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2017. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2017-001 Phase 2 includes study requests in the following cluster groups: 01 - Woodward, 02 - Hitchland, 03 - Spearville, 04 - Northwest Kansas, 06 - South Texas Panhandle/New Mexico, 07 - Southwestern Oklahoma, 08 - North Oklahoma/South Central Kansas, 09 - Nebraska, 13 - Northeast Kansas/Northwest Missouri, 14 - South Central Oklahoma, 15 - Eastern South Dakota, 17 - Western South Dakota (These three groups were included for informational purposes only: 10 - Southeast Oklahoma/Northeast Texas, 12 - Northwest Arkansas, and 16 - Western North Dakota) NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase Two will consist of a power flow analysis, a stability analysis and a short-circuit analysis.
DISIS Manual Version 1.4
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
6093 MW
The minimum cost, including both power flow and stability, of interconnecting all requests included in this DISIS is estimated at:
998058145.75
Models Used in Study
2019 ITP Series
Winter: 2019, 2024
Summer: 2020, 2024, 2029
Light: 2024 & Spring: 2020
By: SPP Generator Interconnection Department
Published: November 03, 2021
Costs for Solar Requests were allocated using the 20SP (summer peak) model.

## Revision History
Revision History
Date | Author | Change Description
4413300% | SPP | Phase 1 Posting
4415300% | SPP | Phase One Report Workbook has been updated to adjust 3.7% of assigned upgrade costs. Updates include Interconnection Upgrades cost adjustment totaling $10,681,245.00 and reallocation of Network Upgrade cost assignments totaling $315,101,329.37. Details regarding all report updates are included in the "Revision Details" tab for tracking.
4429300% | SPP | Phase 2 Posting
4431400% | SPP | Phase 2 Reposting to remove Upgrade no longer assgned
4447700% | SPP | DISIS-2017-001-1: Restudy of Groups 1, 2, 3, 4, 6, 7, 8, 9, 14, 15, & 17 Draft Posting
4449100% | SPP | DISIS-2017-001-1: Restudy of Groups 1, 2, 3, 4, 6, 7, 8, 9, 14, 15, & 17 Draft Update Posting
4450300% | SPP | DISIS-2017-001-1: Restudy of Groups 1,2, 3, 4, 5, 7, 8, 9, 14, 15, & 17 Final Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4431400% | Total Costs Assigned | 1 | Executive Summary | Update total costs assigned.
4431400% | Solutions Update | 5 | Constraints Summary | Update solution for upgrades removed to reflect reason for adjustment (Power Flow)
4431400% | Costs Assigned | 6 | Assigned Upgrade Costs | Remove allocated costs associated with upgrades removed (Power Flow and Stability)
4431400% | Costs Assigned | 7 | Upgrade Summary | Remove upgrades no longer assigned (Power Flow and Stability)
4431400% | Contingenct Upgrades | 6 | Assigned Upgrade Costs | Add upgrades requests are contingent upon
4431400% | Contingenct Upgrades | 7 | Upgrade Summary | Add upgrades requests are contingent upon
4447700% | Total Costs Assigned | 1 | Executive Summary | Updated total costs assigned and updated DISIS Manual version to 1.4
4447700% | Request Data | 4 | Requests | Updated requests tab based on DP2 elections
4447700% | Solutions Update | 5 | Constraints Summary | Updated constraints based on restudy and adjusted solutions
4447700% | Costs Assigned | 6 | Assigned Upgrade Costs | Adjusted cost allocation for remaining requests based on updated solutions
4447700% | Upgrades and Costs | 7 | Upgrade Summary | Updated remaining upgrades based on updated solutions
4447700% | Constraints Observed | 8 | All Thermal | Updated the thermal constraints to reflect the restudy
4449100% | Costs Assigned | 6 | Assigned Upgrade Costs | Updated cost allocation for some of the upgrades
4449100% | Costs Assigned | 7 | Upgrade Summary | Updated cost allocation and cost estimates for some of the upgrades
4449100% | Mitigations | 5 | Constraints Summary | Updated constraints and mitigations listed to account for changes
4449100% | Mitigations | 8 | All Thermal | Updated violations listed in the all thermal tab to account for changes
4449100% | Data Addition | 7 | Assigned Upgrade Costs | Added PTDF column to help provide clarity on cost allocation
4449100% | Data Addition | 4 | Requests | Added limiting element column to help provide clarity on LOIS values
4450300% | Constraints Observed | 5 | Constraints Summary | Updated constraints to reflect invalidation of contingency
4450300% | Costs Assigned | 6 | Assigned Upgrade Costs | Updated cost allocation based on removal upgrade
4450300% | Upgrades and Costs | 7 | Upgrade Summary | Updated costs for a few upgrades and removed upgrade based on invalidation of contingency

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | 163.1 | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | 201.6 | None | ER | SUNC | Elm Creek - Summit 345kV | FACILITY STUDY STAGE
GEN-2017-005 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 190 | 190 | None | ER | WERE | Marmaton - Litchfield 161kV | FACILITY STUDY STAGE
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302 | 294.4 | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | ER | WERE | Neosho - Caney River 345kV | FACILITY STUDY STAGE
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | 0 | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | ER | WAPA | Rhame 230kV Sub | FACILITY STUDY STAGE
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | 151.8 | None | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | 200 | None | ER/NR | SUNC | Mingo 345kV | FACILITY STUDY STAGE
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | 300 | None | ER/NR | WAPA | Philip Tap 230kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 189 | 0 | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | ER/NR | SUNC | Thistle 345kV sub | FACILITY STUDY STAGE
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | ER/NR | SUNC | Post Rock - Spearville 345kV | FACILITY STUDY STAGE
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | 59.1 | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | 84.7 | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | 140 | None | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | ER | SPS | Finney - Lamar 345kV | FACILITY STUDY STAGE
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | 0 | 511456 O.K.U.-7 345 511468 L.E.S.-7 345 1 | ER/NR | AEPW | Oklaunion 345kV sub | FACILITY STUDY STAGE
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | 100 | None | ER | WFEC | Snyder - Cache 138kV | FACILITY STUDY STAGE
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200.1 | 200.1 | None | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | 0 | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | ER | WAPA | Neset 230kV | FACILITY STUDY STAGE
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | 72.5 | None | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 149.4 | None | ER | EMDE | LaRussell Energy Center 161kV | FACILITY STUDY STAGE
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | 101.5 | None | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | 110 | None | ER/NR | WAPA | Underwood - Wayside 230kV | FACILITY STUDY STAGE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | 0 | 532765 HOYT 7 345 532766 JEC N 7 345 1 | ER/NR | WERE | Gordon Evans 138kV | FACILITY STUDY STAGE
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 124.7 | None | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | 52.2 | None | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 72.5 | None | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 71.9 | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | 200 | None | ER | OKGE | Hugo-Sunnyside 345kV | FACILITY STUDY STAGE
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | 52.2 | None | ER | AEPW | Chamber Springs 161kV | FACILITY STUDY STAGE
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 124.7 | None | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 149.4 | None | ER | EMDE | Asbury Plant 161kV | FACILITY STUDY STAGE
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | 0.6 | None | ER/NR | NPPD | Friend 115kV | FACILITY STUDY STAGE
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | 0 | 532765 HOYT 7 345 532766 JEC N 7 345 1 | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | 0 | 541510 HOLT 7 345 645458 S3458 3 345 1 | ER | KCPL | Adrian 161kV sub | FACILITY STUDY STAGE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | 200 | None | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | 200 | None | ER/NR | WAPA | Fort Thompson-Huron 230kV | FACILITY STUDY STAGE
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | 128 | None | ER | WAPA | Underwood 115kV Sub | FACILITY STUDY STAGE
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | 0 | 531449 HOLCOMB7 345 531465 SETAB 7 345 1 | ER/NR | SUNC | Post Rock - Spearville 345kV | FACILITY STUDY STAGE
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | 0 | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 |  |  | ER/NR | AECI | Maryville 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 |  |  | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  |  | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  |  | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 |  |  | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  |  | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  |  | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 |  |  | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 |  |  | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 |  |  | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 |  |  | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 |  |  | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 |  |  | ER | WAPA
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 |  |  | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 |  |  | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 |  |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 |  |  | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 |  |  | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 |  |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 |  |  | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 |  |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  |  | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 |  |  | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 |  |  | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 |  |  | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 |  |  | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 |  |  | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 |  |  | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 |  |  | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 |  |  | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 |  |  | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 |  |  | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 |  |  | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 |  |  | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 |  |  | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 |  |  | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 |  |  | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 |  |  | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 5 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 |  |  | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 |  |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 |  |  | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 |  |  | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 |  |  | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 |  |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 |  |  | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  |  | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 |  |  | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 |  |  | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  |  | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 |  |  | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  |  | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  |  | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  |  | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  |  | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 |  |  | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  |  | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 |  |  | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 |  |  | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 |  |  | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  |  | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  |  | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  |  | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 |  |  | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 |  |  | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 |  |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 |  |  | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 |  |  | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV]
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 |  |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 |  |  | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  |  | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 |  |  | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 |  |  | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 |  |  | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 |  |  | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 |  |  | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 |  |  | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 |  |  | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 |  |  | ER | GRDA | Coffeyville City 69kV
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 |  |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 |  |  | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 |  |  | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 |  |  | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 |  |  | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 |  |  | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 |  |  | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 |  |  | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 |  |  | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 |  |  | ER | GRDA | Ferguson 69kV
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 |  |  | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 |  |  | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 |  |  | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 |  |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 |  |  | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 |  |  | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 |  |  | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 |  |  | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 |  |  | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 |  |  | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 |  |  | ER | SUNC | Garden City 115kV
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 |  |  | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 |  |  | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 |  |  | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 |  |  | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 |  |  | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 |  |  | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 |  |  | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 |  |  | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 |  |  | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 |  |  | ER | SPS | PanTex South 115kV
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 |  |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 |  |  | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 40 |  |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 |  |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 |  |  | ER | OKGE | Redbud 345kV
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 |  |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 |  |  | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 |  |  | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 |  |  | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 |  |  | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 |  |  | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 |  |  | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 |  |  | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 |  |  | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 |  |  | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 |  |  | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 |  |  | ER | WERE | Sheffield 69kV
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 |  |  | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 |  |  | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 |  |  | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 |  |  | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 |  |  | ER | SPS | Pleasant Hill 69kV
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 |  |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 |  |  | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 |  |  | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 |  |  | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  |  | ER | NPPD | John 1 115kV
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 |  |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  |  | ER | NPPD | John 2 115kV
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  |  | ER | NPPD | Jeffrey 115kV
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 |  |  | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 |  |  | ER | SPS | Herring 115kV
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 |  |  | ER | SPS | Hendricks 69kV
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 |  |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 |  |  | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 |  |  | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 |  |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 |  |  | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 |  |  | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 |  |  | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 |  |  | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 |  |  | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 |  |  | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 |  |  | ER | SPS | Lovington 115kV
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 |  |  | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 |  |  | ER | WERE | Westar 6th Street 115kV
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 |  |  | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 |  |  | ER | SPS | Lovington 115kV
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 |  |  | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 |  |  | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 |  |  | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 |  |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 |  |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 |  |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 |  |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 |  |  | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 |  |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 |  |  | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 |  |  | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 |  |  | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 |  |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 |  |  | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 |  |  | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 |  |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 |  |  | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 |  |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 |  |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 |  |  | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 |  |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 |  |  | ER | AECI | Remington 138kV
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  |  | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 |  |  | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 |  |  | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 |  |  | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 |  |  | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  |  | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 |  |  | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  |  | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 |  |  | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  |  | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  |  | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  |  | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 |  |  | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  |  | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 |  |  | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 |  |  | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 |  |  | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 |  |  | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  |  | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 |  |  | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  |  | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 |  |  | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  |  | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 |  |  | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  |  | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 |  |  | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  |  | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 |  |  | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 |  |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 |  |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 |  |  | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 |  |  | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 |  |  | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 |  |  | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 |  |  | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 |  |  | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 |  |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 |  |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  |  | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 |  |  | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 |  |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 |  |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 |  |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 |  |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 |  |  | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 |  |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 |  |  | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 |  |  | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 |  |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 |  |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 |  |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 |  |  | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 |  |  | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 |  |  | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 |  |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 |  |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 |  |  | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 |  |  | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 |  |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 |  |  | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 |  |  | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  |  | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 |  |  | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 |  |  | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 |  |  | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 |  |  | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 |  |  | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 |  |  | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 |  |  | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 |  |  | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 |  |  | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 |  |  | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  |  | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  |  | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 |  |  | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 |  |  | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  |  | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  |  | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 |  |  | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  |  | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 |  |  | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 |  |  | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 |  |  | ER | SPS | Martin 115kV
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 |  |  | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 |  |  | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  |  | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  |  | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  |  | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  |  | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 |  |  | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  |  | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 |  |  | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 |  |  | ER | SPS | Valero 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 |  |  | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 |  |  | ER | OTP

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 20SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z | [7 empty] | Antelope to Holt County 345kV New Line
00NR | NRIS | Non-Converge | Non-Converge | 24SP | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON | [7 empty] | NTC 200220 (Rplan)
00NR | NRIS | Non-Converge | Non-Converge | 24SP | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z | [7 empty] | NTC 200220 (Rplan)
00NR | NRIS | Non-Converge | Non-Converge | 24SP | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192) | [7 empty] | Bison Capacitor 150 MVAR (MISO upgrade )
00NR | NRIS | Thermal | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 | 19WP, 20SP, 24SP, 24WP, 29SP | P13:069-138:WERE:MONT_TX-1_138-69:: |  | 36 | 89.53 | 109.75 |  |  |  | Altoona 69kV Terminal Upgrades (DISIS-2017-001)
00NR | NRIS | Thermal | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 | 19WP, 20SP, 24SP, 24WP, 29SP | P23:345:SUNC:HLC_BRK382 |  | 80 | 127.02 | 133.79 |  |  |  | ALXNDR to NESCTY 115kV Rebuild (DISIS-2017-001)
00NR | NRIS | Thermal | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 24SP | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT |  | 956 | 94.12 | 101.89 |  |  |  | NTC 200220 (Rplan)
00NR | NRIS | Thermal | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 24SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT |  | 956 | 94.12 | 101.89 |  |  |  | NTC 200220 (Rplan)
00NR | NRIS | Thermal | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 24SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z |  | 956 | 93.84 | 101.37 |  |  |  | NTC 200220 (Rplan)
00NR | NRIS | Thermal | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 | 24SP | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z |  | 120 | 80.25 | 99.8 |  |  |  | NTC 200220 (Rplan)
00NR | NRIS | Thermal | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 | 20SP, 24SP, 29SP | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT |  | 352 | 111.05 | 125.36 |  |  |  | Appledorn to Watertown 230kV Rebuild (DISIS-2017-001)
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 | 19WP, 24SP, 24WP, 29SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 113.17 | 121.06 |  |  |  | MISO R.A.S.
00NR | NRIS | Thermal | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 24SP | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z |  | 320 | 86.33 | 101.59 |  |  |  | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA)
00NR | NRIS | Thermal | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 20SP, 24SP | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z |  | 320 | 90.38 | 105.87 |  |  |  | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001)
00NR | NRIS | Thermal | 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 | 20SP, 29SP | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT |  | 409 | 91.9 | 103.96 |  |  |  | Granite Falls to Appledorn 230kV Rebuild (DISIS-2017-001)
00NR | NRIS | Thermal | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 20SP, 24SP, 24WP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 120 | 122.77 | 131.46 |  |  |  | ITP Model update of GARRISN7 to PICKCITY-RR7 115 kV
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 19WP, 20SP, 24SP, 24WP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 120 | 124.09 | 132.79 |  |  |  | ITP Model update of STANTN.T-BE7 to PICKCITYU-RR7 115 kV
00NR | NRIS | Thermal | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 | 20SP, 24SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 88 | 80.32 | 108.61 |  |  |  | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA), Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC)
00NR | NRIS | Thermal | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 | 20SP, 24SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 88 | 76.68 | 104.87 |  |  |  | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA), Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC)
00NR | NRIS | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 20SP, 24SP, 24WP, 29SP | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 |  | 720 | N/A | 130.79 |  |  |  | Model Correction
00NR | NRIS | Thermal | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 20SP, 24SP, 24WP, 29SP | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1 |  | 720 | N/A | 130.31 |  |  |  | Model Correction
00NR | NRIS | Thermal | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 | 19WP, 20SP, 24SP, 24WP, 29SP | P13:069-138:WERE:MONT_TX-1_138-69:: |  | 36 | 89.53 | 109.75 |  |  |  | Neodesha Jct. 69kV Terminal Upgrades (DISIS-2017-001)
00NR | NRIS | Thermal | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 | 24SP | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z |  | 120 | 81.99 | 102.7 |  |  |  | Phillip to Wanblee 115kV Rebuild (DISIS-2017-001) (WAPA)
00NR | NRIS | Thermal | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 | 20SP, 24SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 478 | 93.73 | 105.53 |  |  |  | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (BEPC), Sidney_MB4 Terminal Upgrades (DISIS-2017-001) (BEPC), Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (MRES), Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (LES), Sidney_TS4 230kV Terminal Upgrades (DISIS-2017-001) (BEPC)
00NR | NRIS | Thermal | 659210 SIDNEY__-MB4 230 997086 SDQ KV2A 230 1 | 20SP, 24SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 496 | 92.18 | 103.72 |  |  |  | Sidney_MB3 345kV New Transformer (DISIS-2017-001)
00NR | NRIS | Thermal | 635000 CBLUFFS3 345 645456 S3456 3 345 1 | 29SP | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) |  | 956 | 42.04 | 103.42 |  |  |  | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (MEC), Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (OPPD)
00NR | NRIS | Thermal | 541199 ST JOE 3 345 640139 COOPER 3 345 1 | 24WP | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS |  | 1195 | 102.3 | 104.18 |  |  |  | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (GMO), St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD), Cooper 345kV Terminal Upgrades (DISIS-2017-001)
00NR | NRIS | Thermal | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | 24WP, 29SP | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE |  | 1195 | 109.16 | 111.42 |  |  |  | St. Joe to Nashua 345kV Rebuild (DISIS-2017-001) (KCPL), St. Joe 345kV Terminal Upgrades for Nashua Rebuild (DISIS-2017-001) (GMO)
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 | 19WP, 24SP, 24WP, 29SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 113.17 | 121.06 |  |  |  | MISO R.A.S.
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 | 19WP, 24SP, 24WP, 29SP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 113.17 | 121.06 |  |  |  | MISO R.A.S.
00NR | NRIS | Thermal | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 29SP | P12:115:SPS:V24.1.WOLFTH.TERRY |  | 318.7 | 97.96 | 100.88 |  |  |  | Model Correction for Sundown to Wolfforth 230kV (DISIS-2017-001)
00NR | NRIS | Thermal | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 | 20SP, 24SP | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 88 | 85.33 | 102.85 |  |  |  | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA), Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC)
00NR | NRIS | Thermal | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 | 20SP, 24SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 88 | 76.68 | 104.87 |  |  |  | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA), Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC)
01ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
01ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Woodward 345kV New Line (DISIS-2017-001)
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Woodward 345kV New Line (DISIS-2017-001)
02ALL | ERIS | Thermal | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1 | 24L | System Intact | 389.2 |  | 103.23 | 104.11 |  |  |  | Model Correction - 21ITP uprate to Rate A = 490MVA, Rate B = 540 MVA
03ALL | ERIS | Non-Converge | Non-Converge | 29SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) | [7 empty] | Finney 345kV Reactive Support (DISIS-2017-001)
03ALL | ERIS | Non-Converge | Non-Converge | 29SP | P23:345:SUNC:HLC_BRK188 | [7 empty] | Finney 345kV Reactive Support (DISIS-2017-001)
03ALL | ERIS | Non-Converge | Non-Converge | 29SP | P23:345:SUNC:HLC_BRK282 | [7 empty] | Finney 345kV Reactive Support (DISIS-2017-001)
03ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 588754 G17-032-TAP 345 1 | 29SP | System Intact | 380 |  | 60.74 | 110.65 |  |  |  | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001)
03ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 24L | System Intact | 319 |  | 98.32 | 110.14 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW), Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE)
04ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
04ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
06ALL | ERIS | Non-Converge | Non-Converge | 24L, 24SP, 24WP | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | [7 empty] | Border 345kV Reactive Support NTC 210609
06ALL | ERIS | Non-Converge | Non-Converge | 24L, 24SP, 24WP | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB | [7 empty] | Border 345kV Reactive Support NTC 210609
06ALL | ERIS | Non-Converge | Non-Converge | 24L, 24SP, 24WP | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | [7 empty] | Border 345kV Reactive Support NTC 210609
06ALL | ERIS | Non-Converge | Non-Converge | 24L, 24SP, 24WP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | [7 empty] | Border 345kV Reactive Support NTC 210609
06ALL | ERIS | Non-Converge | Non-Converge | 24L, 24SP, 24WP | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT | [7 empty] | Border 345kV Reactive Support NTC 210609
06ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
07ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
07ALL | ERIS | Thermal | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 | 29SP | P12:345:OKGE-AEPW:BKRBKR371 |  | 318.7 | 67.64 | 104.29 |  |  |  | 2020 ITP Model Update that Taps Woodward to Border approximately 19 miles from Border, and Hairpin both lines into Chisholm 345 kV. Include 50 MVAR reactor at Chisholm 345kV
07ALL | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 29SP | P42:345:OKGE:SB_GRNT7313 |  | 395 | 77.86 | 113.33 |  |  |  | 2020 ITP Model Update that Taps Woodward to Border approximately 19 miles from Border, and Hairpin both lines into Chisholm 345 kV. Include 50 MVAR reactor at Chisholm 345kV
07ALL | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 20SP, 24L, 24SP, 29SP | P42:345:OKGE:SB_GRNT7313 |  | 353 | 87.09 | 126.83 |  |  |  | 2020 ITP Model Update that Taps Woodward to Border approximately 19 miles from Border, and Hairpin both lines into Chisholm 345 kV. Include 50 MVAR reactor at Chisholm 345kV
07ALL | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24L, 24SP, 24WP, 29SP | P42:345:OKGE:SB_GRNT7313 |  | 234 | 82.43 | 117.6 |  |  |  | GEN-2015-093 breaker addition NTC Project ID 51332/Upgrade ID 82127
08ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
08ALL | ERIS | Thermal | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 24L | System Intact | 247 |  | 95.26 | 100.7 |  |  |  | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP), Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA)
08ALL | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 20SP, 24SP, 29SP | System Intact | 1036 |  | 107.37 | 107.38 |  |  |  | Hoyt - JEC 345kV Rebuild (DISIS-2017-001)
08ALL | ERIS | Thermal | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 20G, 20SP, 24L, 24SP, 29SP | System Intact | 205 |  | 114.88 | 121.31 |  |  |  | ITP Model Update of Neosho to Riviera 161 kV
08ALL | ERIS | Thermal | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:WERE:WAVS-LACY_345:: |  | 956 | 101.25 | 123.22 |  |  |  | Wolf Creek to Blackberry 345kV
08ALL | ERIS | Thermal | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 20G, 24L | System Intact | 1141 |  | 106.54 | 109.9 |  |  |  | Wolf Creek to Blackberry 345kV
09ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
09ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
10ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
10ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
12ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
12ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO), Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO)
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO), Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO)
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P22:345:GMO-OPPD:S3458-HOLT | [7 empty] | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO), Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO)
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:OPPD:S3458-HOLT | [7 empty] | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO), Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO)
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P44:345:OPPD:S3458-HOL&R1 | [7 empty] | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO), Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO)
13ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
14ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP | P12:345:AEPW-WFEC:VALIANT7:HUGO7 |  | 287 | 79.78 | 102.61 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC)
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP | P23:345:AEPW:VALLIANT CB 3413A NBTB |  | 287 | 77.29 | 99.5 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC)
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT |  | 287 | 77.29 | 99.5 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC)
15ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
15ALL | ERIS | Thermal | None | N/A | None | [7 empty] | None
15NR | NRIS | Thermal | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z | 20G | P23:345:MEC:RAUN 0270 |  | 341 | 139.76 | 141.39 |  |  |  | Sioux City 230 kV Substation Upgrade (DISIS-2017-001)
16ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 29SP | System Intact | 400 |  | 98.18 | 108.83 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 24SP | System Intact | 400 |  | 102.33 | 112.41 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 20SP | System Intact | 400 |  | 99.51 | 109.59 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 29SP | System Intact | 400 |  | 101.01 | 113.27 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 24SP | System Intact | 400 |  | 105.68 | 117.6 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 20SP | System Intact | 400 |  | 102.51 | 114.17 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 20G | System Intact | 400 |  | 87.36 | 100.16 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001)
16ALL | ERIS | Thermal | 652468 HEBRON 4 230 661053 MANDAN 4 230 1 | 20SP, 24SP, 29SP | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1 |  | 264 | 84.53 | 113.27 |  |  |  | Model Correction
16ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z |  | 506 | 86.69 | 140.65 |  |  |  | Neset - Northshore 230 kV Ckt 1
17ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
17ALL | ERIS | Thermal | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  | 0 | 184.77 |  |  |  | ITP Model update of GEN-2017-014 to Phillip Tap 230 kV
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.11 | 119.22 |  |  |  | Rebuild Ogalala to Sidney 230 kV Line (DISIS-2017-001)

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2016-037 | 07 - Southwestern Oklahoma | 82127 | ERIS | GEN-2015-093 Circuit Breaker Addition to Gracemont 138kV substation | Contingent | GEN-2015-093 to add a circuit breaker to the Gracemont 138kV substation as an interconnection upgrade. | 0 | 0% | 1145042 | N/A
GEN-2016-037 | 07 - Southwestern Oklahoma | NTC 2010575/210587 | ERIS | Multi - Border - Woodward 345 kV Tap NTC 210575/210587 | Contingent | Tap Woodward to Border approximately 19 miles from Border. Hairpin both lines into Chisholm 345 kV. Include 50 MVAR reactor at Chisholm 345kV. | 0 | 0% | 24360634 | N/A
GEN-2016-037 | 07 - Southwestern Oklahoma | 132903 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 20639740 | 100% | 20639740 | 1
GEN-2016-037 | 07 - Southwestern Oklahoma | 143127 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 15000 | 100% | 15000 | 1
GEN-2016-037 | 07 - Southwestern Oklahoma | 132902 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 1146800 | 100% | 1146800 | 1
GEN-2017-004 | 04 - Northwest Kansas | 132937 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | 15081109 | 100% | 15081109 | 1
GEN-2017-004 | 04 - Northwest Kansas | 132936 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | 1054767 | 100% | 1054767 | 1
GEN-2017-005 | 12 - Northwest Arkansas | 132939 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | 11434328 | 100% | 11434328 | 1
GEN-2017-005 | 12 - Northwest Arkansas | 132938 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | 1216477 | 100% | 1216477 | 1
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178 | N/A
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 132947 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | 15017048 | 100% | 15017048 | 1
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 132946 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | 1311181 | 100% | 1311181 | 1
GEN-2017-010 | 16 - Western North Dakota | 122669 | ERIS | Leland Olds 345 kV Substation Reconfiguration (DISIS-2016-002-2) | Contingent | Construct one (1) new 345 kV breaker | 0 | 0% | 4600000 | N/A
GEN-2017-010 | 16 - Western North Dakota | 143226 | ERIS | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Current Study | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | 2019128.29 | 34.19% | 5906325 | 1
GEN-2017-010 | 16 - Western North Dakota | 132949 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Construct one (1) 230kV breaker, one (1) 230kV breaker disconnect switch, one (1) set of line PTs, one (1) set of CTs, one (1) set of line surge arrestors and all other associated work and materials. | 1122522 | 100% | 1122522 | 1
GEN-2017-010 | 16 - Western North Dakota | 132948 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | Interconnection | Construct one (1) 230 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility. | 1674744 | 100% | 1674744 | 1
GEN-2017-011 | 01 - Woodward | 132951 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | 15000 | 100% | 15000 | 1
GEN-2017-011 | 01 - Woodward | 132950 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | 0 | 100% | 0 | 1
GEN-2017-013 | 04 - Northwest Kansas | 132955 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | 3269931 | 100% | 3269931 | 1
GEN-2017-013 | 04 - Northwest Kansas | 132954 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | 2447857 | 100% | 2447857 | 1
GEN-2017-013 | 04 - Northwest Kansas | 144272 | NRIS | ALXNDR to NESCTY 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing ALXNDR to NESCTY 115kV 18.03 mile line to achieve a minimum winter/emergency rating of 110 MVA | 12816445.2 | 100% | 12816445.2 | 1
GEN-2017-013 | 04 - Northwest Kansas | 122699 | NRIS | Antelope to Holt County 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 20 miles of new 345kV line from Antelope to Holt County | 15385551.87 | 21.98% | 70000000 | 0.2347
GEN-2017-013 | 04 - Northwest Kansas | 144267 | NRIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Cooper 345kV to achieve a minimum winter/emergency rating of 1245 MVA | 0 | 56.84% | 0 | 0.3604
GEN-2017-013 | 04 - Northwest Kansas | 143269 | NRIS | St. Joe 345kV Terminal Upgrades for Nashua Rebuild (DISIS-2017-001) (GMO) | Current Study | Upgrade terminal equipment at St. Joe 345kV to achieve a minimum winter/emergency rating of 1335 MVA | 0 | 76.91% | 0 | 0.6076
GEN-2017-013 | 04 - Northwest Kansas | 143266 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (GMO) | Current Study | Rebuild the existing St. Joe to Cooper 345kV 38 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | 24718841.7442 | 56.84% | 43488872 | 0.3604
GEN-2017-013 | 04 - Northwest Kansas | 144265 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild the existing St. Joe to Cooper 345kV 26.61 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | 17309694.1566 | 56.84% | 30453654.8 | 0.3604
GEN-2017-013 | 04 - Northwest Kansas | 144268 | NRIS | St. Joe to Nashua 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild the existing St. Joe to Nashua 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1335 MVA | 33976344.2461 | 76.91% | 44175538.4 | 0.6076
GEN-2017-014 | 17 - Western South Dakota | NTC 200220 | ERIS | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0% | 412074343 | N/A
GEN-2017-014 | 17 - Western South Dakota | 122699 | NRIS | Antelope to Holt County 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 20 miles of new 345kV line from Antelope to Holt County | 42665898.75 | 60.95% | 70000000 | 0.4339
GEN-2017-014 | 17 - Western South Dakota | N/A | ERIS | GEN-2017-014 230kV Reactive Support (DISIS-2017-001) | Interconnection | Stability identified need to install 30 MVar SVC for Dynamic Reactive Support at GEN-2017-014 230kV Side of Main Transformer | 6788460 | 100% | 6788460 | 1
GEN-2017-014 | 17 - Western South Dakota | 132957 | ERIS | Philip Tap 230 kV GEN-2017-014 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Philip Tap 230 kV. | 8500000 | 100% | 8500000 | 1
GEN-2017-014 | 17 - Western South Dakota | 132956 | ERIS | Philip Tap 230 kV GEN-2017-014 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Philip Tap 230 kV. | 0 | 100% | 0 | 1
GEN-2017-014 | 17 - Western South Dakota | 143307 | NRIS | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Fort Randall to Lake Platte 43.34 mile line to achieve a minimum summer/emergency rating of 330 MVA | 1112812.5764 | 55.64% | 2000000 | 0.4554
GEN-2017-014 | 17 - Western South Dakota | 143306 | NRIS | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Fort Thompson to Fort Randall 87.32 mile line to achieve a minimum summer/emergency rating of 340 MVA | 13113235.2 | 55.64% | 23568000 | 0.4554
GEN-2017-014 | 17 - Western South Dakota | 143304 | NRIS | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA | 127620.09 | 73.3% | 174097 | 0.5017
GEN-2017-014 | 17 - Western South Dakota | 143316 | NRIS | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 95 MVA | 432493.6807 | 73.3% | 590000 | 0.5017
GEN-2017-014 | 17 - Western South Dakota | 144271 | NRIS | Phillip to Wanblee 115kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/normal rating of 125 MVA | 18400000 | 100% | 18400000 | 1
GEN-2017-014 | 17 - Western South Dakota | 143301 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (MEC) | Current Study | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 3.34 mile line to achieve a minimum winter/emergency rating of 990 MVA | 5158606 | 100% | 5158606 | 1
GEN-2017-014 | 17 - Western South Dakota | 143300 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 5.63 mile line section to achieve a minimum winter/emergency rating of 990 MVA | 2510992 | 100% | 2510992 | 1
GEN-2017-014 | 17 - Western South Dakota | 144274 | NRIS | Sidney_MB3 345kV New Transformer (DISIS-2017-001) | Current Study | Replace the existing Sidney_MB3 345/230kV transformer to achieve a minimum summer/normal rating of 515 MVA | 3946055.8867 | 47.53% | 8302968 | 0.2493
GEN-2017-014 | 17 - Western South Dakota | 144264 | NRIS | Sidney_MB4 Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Sidney_MB4 230kV to achieve a minimum summer emergency rating of 510 MVA | 0 | 50.7% | 0 | 0.2738
GEN-2017-014 | 17 - Western South Dakota | 143260 | NRIS | Sidney_TS4 230kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Sidney_TS4 230kV to achieve a minimum summer emergency rating of 510 MVA | 0 | 50.7% | 0 | 0.2738
GEN-2017-014 | 17 - Western South Dakota | 143261 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (BEPC) | Current Study | Rebuild the existing .65 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | 291142.1228 | 50.7% | 574280.85 | 0.2738
GEN-2017-014 | 17 - Western South Dakota | 143262 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (LES) | Current Study | Rebuild the existing 1.35 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | 604679.7935 | 50.7% | 1192737.15 | 0.2738
GEN-2017-014 | 17 - Western South Dakota | 144263 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (MRES) | Current Study | Rebuild the existing 2.0 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | 895821.92 | 50.7% | 1767018 | 0.2738
GEN-2017-014 | 17 - Western South Dakota | 143305 | NRIS | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA | 0 | 73.3% | 0 | 0.5017
GEN-2017-014 | 17 - Western South Dakota | 143315 | NRIS | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 95 MVA | 0 | 73.3% | 0 | 0.5017
GEN-2017-018 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +200 MVAR Capacitor Bank(s) at Finney 345kV | 190808.69 | 1.5% | 12734040 | 0.015
GEN-2017-018 | 03 - Spearville | 132961 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 1412092 | 100% | 1412092 | 1
GEN-2017-018 | 03 - Spearville | 143117 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 30000 | 100% | 30000 | 1
GEN-2017-018 | 03 - Spearville | 143118 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 13299 | 100% | 13299 | 1
GEN-2017-018 | 03 - Spearville | 132960 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 918132 | 100% | 918132 | 1
GEN-2017-021 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +200 MVAR Capacitor Bank(s) at Finney 345kV | 2857755.49 | 22.44% | 12734040 | 0.2123
GEN-2017-021 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 7047231.6759 | 42.71% | 16500000 | 0.3859
GEN-2017-021 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 11670064.4602 | 42.71% | 27323646 | 0.3859
GEN-2017-021 | 03 - Spearville | 132963 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 7540554.5 | 100% | 7540554.5 | 1
GEN-2017-021 | 03 - Spearville | 132962 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 527383.5 | 100% | 527383.5 | 1
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 132965 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | 4790295 | 100% | 4790295 | 1
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 132964 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | 696118 | 100% | 696118 | 1
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143295 | NRIS | Altoona 69kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Altoona to Neodesha Jct. to achieve a minimum summer/emergency rating of 40 MVA | 3325 | 100% | 3325 | 1
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 144267 | NRIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Cooper 345kV to achieve a minimum winter/emergency rating of 1245 MVA | 0 | 15.26% | 0 | 0.2871
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143296 | NRIS | Neodesha Jct. 69kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Neodesha Jct. to achieve a minimum summer/emergency rating of 40 MVA | 0 | 100% | 0 | 1
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143269 | NRIS | St. Joe 345kV Terminal Upgrades for Nashua Rebuild (DISIS-2017-001) (GMO) | Current Study | Upgrade terminal equipment at St. Joe 345kV to achieve a minimum winter/emergency rating of 1335 MVA | 0 | 4.42% | 0 | 0.1074
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 143266 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (GMO) | Current Study | Rebuild the existing St. Joe to Cooper 345kV 38 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | 6638216.1438 | 15.26% | 43488872 | 0.2978
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 144265 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild the existing St. Joe to Cooper 345kV 26.61 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | 4648498.1935 | 15.26% | 30453654.8 | 0.2978
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 144268 | NRIS | St. Joe to Nashua 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild the existing St. Joe to Nashua 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1335 MVA | 1951850.3883 | 4.418% | 44175538.4 | 0.1074
GEN-2017-023 | 14 - South Central Oklahoma | 143243 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | Current Study | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 295 MVA | 1490000 | 100% | 1490000 | 1
GEN-2017-023 | 14 - South Central Oklahoma | 132967 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | 0 | 100% | 0 | 1
GEN-2017-023 | 14 - South Central Oklahoma | 132966 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | 750000 | 100% | 750000 | 1
GEN-2017-027 | 14 - South Central Oklahoma | 132973 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | 1396000 | 100% | 1396000 | 1
GEN-2017-027 | 14 - South Central Oklahoma | 132972 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | 515000 | 100% | 515000 | 1
GEN-2017-032 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +200 MVAR Capacitor Bank(s) at Finney 345kV | 7542159.21 | 59.23% | 12734040 | 0.5603
GEN-2017-032 | 03 - Spearville | 143228 | ERIS | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Finney to G17-032 Tap 345kV 78.75 mile line to achieve a minimum Summer/Emergency rating of 425 MVA | 150000 | 100% | 150000 | 1
GEN-2017-032 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 4167344.5671 | 25.26% | 16500000 | 0.2282
GEN-2017-032 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 6901033.1947 | 25.26% | 27323646 | 0.2282
GEN-2017-032 | 03 - Spearville | 132981 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | 12750261 | 100% | 12750261 | 1
GEN-2017-032 | 03 - Spearville | 132980 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | 1708037 | 100% | 1708037 | 1
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | NTC 2010609 | ERIS | Border 345kV Reactive Support NTC 210609 | Contingent | Add 275 MVAR of reactive support at Border 345 kV | 0 | 0% | 3996000 | N/A
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 132983 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 3877147.5 | 100% | 3877147.5 | 1
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 132982 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 1373275 | 100% | 1373275 | 1
GEN-2017-036 | 07 - Southwestern Oklahoma | 132985 | ERIS | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | 8198087 | 100% | 8198087 | 1
GEN-2017-036 | 07 - Southwestern Oklahoma | 132984 | ERIS | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | 1337068 | 100% | 1337068 | 1
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 132993 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | 5741321 | 100% | 5741321 | 1
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 132992 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | 599979 | 100% | 599979 | 1
GEN-2017-047 | 02 - Hitchland | 143693 | ERIS | Beaver County to Woodward 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 60 miles of new 345kV line from Beaver County to Woodward | 64315399.4222 | 49.47% | 130000000 | 0.4962
GEN-2017-047 | 02 - Hitchland | 132997 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | 13148764 | 100% | 13148764 | 1
GEN-2017-047 | 02 - Hitchland | 132996 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | 759404 | 100% | 759404 | 1
GEN-2017-048 | 16 - Western North Dakota | 122669 | ERIS | Leland Olds 345 kV Substation Reconfiguration (DISIS-2016-002-2) | Contingent | Construct one (1) new 345 kV breaker | 0 | 0% | 4600000 | N/A
GEN-2017-048 | 16 - Western North Dakota | NTC 210560 | ERIS | Neset - Northshore 230 kV Ckt 1 NTC 210560 | Contingent | Build new 28 mile 230kV line from Neset to Northshore. | 0 | 0% | 33155575 | N/A
GEN-2017-048 | 16 - Western North Dakota | 143226 | ERIS | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Current Study | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | 3887196.71 | 65.81% | 5906325
GEN-2017-048 | 16 - Western North Dakota | 132999 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Construct one (1) 230kV breaker, one (1) 230kV breaker disconnect switch, one (1) set of line PT, one (1) set of CTs, one (1) set of line surge arrestors and all other associated work and materials. | 1296018 | 100% | 1296018 | 1
GEN-2017-048 | 16 - Western North Dakota | 132998 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | Interconnection | Construct one (1) 230 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility. | 1683828 | 100% | 1683828 | 1
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 133013 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Rebuild Hosston 69kV as a five (5) breaker ring bus to include control panels, line relaying, disconnect switches, structures, foundations, conductors, insulators, and all other associated work and materials. | 17635037 | 100% | 17635037 | 1
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 133012 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (TOIF) (AEPW) | Interconnection | Construct one (1) 69 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility | 1086124 | 100% | 1086124 | 1
GEN-2017-060 | 12 - Northwest Arkansas | 133019 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-060 | 12 - Northwest Arkansas | 133018 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 133021 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | 0 | 100% | 0 | 1
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 133020 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | 4548000 | 100% | 4548000 | 1
GEN-2017-064 | 17 - Western South Dakota | 133023 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | 7102723 | 100% | 7102723 | 1
GEN-2017-064 | 17 - Western South Dakota | 133022 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | 311770 | 100% | 311770 | 1
GEN-2017-064 | 17 - Western South Dakota | NTC 200220 | ERIS | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0% | 412074343 | N/A
GEN-2017-064 | 17 - Western South Dakota | 122699 | NRIS | Antelope to Holt County 345kV New Line (DISIS-2017-001) (NPPD) | Current Study | Build approximately 20 miles of new 345kV line from Antelope to Holt County | 11948549.38 | 17.07% | 70000000 | 0.3314
GEN-2017-064 | 17 - Western South Dakota | 144275 | ERIS | Rebuild Ogalala to Sidney 230 kV Line (DISIS-2017-001) | Current Study | Rebuild the existing Ogalala to Sidney 230kV 68.85 mile line to achieve a minimum summer rating of 400 MVA | 60829594.65 | 100% | 60829594.65 | 1
GEN-2017-064 | 17 - Western South Dakota | 143304 | NRIS | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA | 46476.91 | 26.7% | 174097 | 0.4983
GEN-2017-064 | 17 - Western South Dakota | 143316 | NRIS | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 95 MVA | 157506.3193 | 26.7% | 590000 | 0.4983
GEN-2017-064 | 17 - Western South Dakota | 144274 | NRIS | Sidney_MB3 345kV New Transformer (DISIS-2017-001) | Current Study | Replace the existing Sidney_MB3 345/230kV transformer to achieve a minimum summer/normal rating of 515 MVA | 4356912.1133 | 52.47% | 8302968 | 0.7507
GEN-2017-064 | 17 - Western South Dakota | 144264 | NRIS | Sidney_MB4 Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Sidney_MB4 230kV to achieve a minimum summer emergency rating of 510 MVA | 0 | 49.3% | 0 | 0.7262
GEN-2017-064 | 17 - Western South Dakota | 143260 | NRIS | Sidney_TS4 230kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Sidney_TS4 230kV to achieve a minimum summer emergency rating of 510 MVA | 0 | 49.3% | 0 | 0.7262
GEN-2017-064 | 17 - Western South Dakota | 143261 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (BEPC) | Current Study | Rebuild the existing .65 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | 283138.7272 | 49.3% | 574280.85 | 0.7262
GEN-2017-064 | 17 - Western South Dakota | 143262 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (LES) | Current Study | Rebuild the existing 1.35 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | 588057.3565 | 49.3% | 1192737.15 | 0.7262
GEN-2017-064 | 17 - Western South Dakota | 144263 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (MRES) | Current Study | Rebuild the existing 2.0 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | 871196.08 | 49.3% | 1767018 | 0.7262
GEN-2017-064 | 17 - Western South Dakota | 143305 | NRIS | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA | 0 | 26.7% | 0 | 0.4983
GEN-2017-064 | 17 - Western South Dakota | 143315 | NRIS | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | Current Study | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 95 MVA | 0 | 26.7% | 0 | 0.4983
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178 | N/A
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 122705 | ERIS | Hoyt - JEC 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing JEC - Hoyt 345 kV line as double circuit 345 kV with normal/minimal emergency rating of 1792 MVA. | 24442628.483 | 45.68% | 53508060 | 0.5493
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 133031 | ERIS | Gordon Evans 138 kV Substation GEN-2017-068 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Gordon Evans 138 kV Substation. | 1029997 | 100% | 1029997 | 1
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 133030 | ERIS | Gordon Evans 138 kV Substation GEN-2017-068 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Gordon Evans 138 kV Substation. | 657422 | 100% | 657422 | 1
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 144267 | NRIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Cooper 345kV to achieve a minimum winter/emergency rating of 1245 MVA | 0 | 27.9% | 0 | 0.3382
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143269 | NRIS | St. Joe 345kV Terminal Upgrades for Nashua Rebuild (DISIS-2017-001) (GMO) | Current Study | Upgrade terminal equipment at St. Joe 345kV to achieve a minimum winter/emergency rating of 1335 MVA | 0 | 18.67% | 0 | 0.285
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 143266 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (GMO) | Current Study | Rebuild the existing St. Joe to Cooper 345kV 38 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | 12131814.112 | 27.9% | 43488872 | 0.3418
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 144265 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Current Study | Rebuild the existing St. Joe to Cooper 345kV 26.61 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | 8495462.4499 | 27.9% | 30453654.8 | 0.3418
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 144268 | NRIS | St. Joe to Nashua 345kV Rebuild (DISIS-2017-001) (KCPL) | Current Study | Rebuild the existing St. Joe to Nashua 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1335 MVA | 8247343.7656 | 18.67% | 44175538.4 | 0.285
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 133035 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 1721000 | 100% | 1721000 | 1
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 133034 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 515000 | 100% | 515000 | 1
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 133037 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 1721000 | 100% | 1721000 | 1
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 133036 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 515000 | 100% | 515000 | 1
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 133039 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | 50000 | 100% | 50000 | 1
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 133038 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | 1103400 | 100% | 1103400 | 1
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 143265 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | Current Study | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 250 MVA | 2500000 | 100% | 2500000 | 1
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 143264 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | Current Study | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 250 MVA | 5869344 | 100% | 5869344 | 1
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 133041 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | 1365027 | 100% | 1365027 | 1
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 133040 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | 1146800 | 100% | 1146800 | 1
GEN-2017-075 | 14 - South Central Oklahoma | 133043 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | 1430000 | 100% | 1430000 | 1
GEN-2017-075 | 14 - South Central Oklahoma | 133042 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | 915000 | 100% | 915000 | 1
GEN-2017-076 | 12 - Northwest Arkansas | 133045 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Construct one (1) new 345kV breaker, control panels, line relaying, disconnect switches, structures, foundations, conductors, insulators, and all other associated work and materials. | 1419431 | 100% | 1419431 | 1
GEN-2017-076 | 12 - Northwest Arkansas | 133044 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (TOIF) (AEPW) | Interconnection | Construct one (1) 161 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility. | 1125771 | 100% | 1125771 | 1
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 133047 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | 10334726 | 100% | 10334726 | 1
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 133046 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | 1146800 | 100% | 1146800 | 1
GEN-2017-082 | 12 - Northwest Arkansas | 133057 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-082 | 12 - Northwest Arkansas | 143123 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-082 (149.4 MW/Wind), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 6649 | 100% | 6649 | 1
GEN-2017-082 | 12 - Northwest Arkansas | 133056 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-085 | 09 - Nebraska | 133063 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-085 | 09 - Nebraska | 133062 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 122598 | ERIS | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0% | 142601178 | N/A
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 122705 | ERIS | Hoyt - JEC 345kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing JEC - Hoyt 345 kV line as double circuit 345 kV with normal/minimal emergency rating of 1792 MVA. | 29065431.517 | 54.32% | 53508060 | 0.4507
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 143125 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 20000 | 100% | 20000 | 1
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 133065 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 38569 | 100% | 38569 | 1
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 133064 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 143731 | ERIS | Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | Current Study | Upgrade terminal equipment at Mullin Creek 345kV to accept Mullin Creek to St. Joseph new line | 7665143 | 100% | 7665143 | 1
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 143699 | ERIS | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO) | Current Study | Build approximately 27 miles of new 345kV line from Mullin Creek to St. Joe | 102826609 | 100% | 102826609 | 1
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 133069 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | 10177602 | 100% | 10177602 | 1
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 133068 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | 824356 | 100% | 824356 | 1
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 133073 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | 5741321 | 100% | 5741321 | 1
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 133072 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | 599979 | 100% | 599979 | 1
GEN-2017-094 | 15 - Eastern South Dakota | NTC 200220 | ERIS | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0% | 412074343 | N/A
GEN-2017-094 | 15 - Eastern South Dakota | 144297 | NRIS | Sioux City 230 kV Substation Upgrade (DISIS-2017-001) | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum winter/emergency rating of 630 MVA | 6000000 | 100% | 6000000 | 1
GEN-2017-094 | 15 - Eastern South Dakota | 122574 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | 9000000 | 100% | 9000000 | 1
GEN-2017-094 | 15 - Eastern South Dakota | 122573 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | 250000 | 100% | 250000 | 1
GEN-2017-094 | 15 - Eastern South Dakota | 143309 | NRIS | Appledorn to Watertown 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Watertown to Appledorn 230kV 55.3 mile line to achieve a minimum summer/emergency rating of 450 MVA | 10000000 | 100% | 10000000 | 1
GEN-2017-094 | 15 - Eastern South Dakota | 143307 | NRIS | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA) | Current Study | Rebuild the existing Fort Randall to Lake Platte 43.34 mile line to achieve a minimum summer/emergency rating of 330 MVA | 887187.4236 | 44.36% | 2000000 | 0.5446
GEN-2017-094 | 15 - Eastern South Dakota | 143306 | NRIS | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Fort Thompson to Fort Randall 87.32 mile line to achieve a minimum summer/emergency rating of 340 MVA | 10454764.8 | 44.36% | 23568000 | 0.5446
GEN-2017-094 | 15 - Eastern South Dakota | 144270 | NRIS | Granite Falls to Appledorn 230kV Rebuild (DISIS-2017-001) | Current Study | Rebuild the existing Granite Falls to Appledorn 230kV 19.24 mile line to achieve a minimum summer/emergency rating of 430 MVA | 16998713.2 | 100% | 16998713.2 | 1
GEN-2017-097 | 17 - Western South Dakota | 133077 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | 0 | 100% | 0 | 1
GEN-2017-097 | 17 - Western South Dakota | 133076 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | 1208190 | 100% | 1208190 | 1
GEN-2017-099 | 03 - Spearville | 143263 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | Current Study | Install +200 MVAR Capacitor Bank(s) at Finney 345kV | 2143316.61 | 16.83% | 12734040 | 0.2123
GEN-2017-099 | 03 - Spearville | 143240 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 5285423.757 | 32.03% | 16500000 | 0.3859
GEN-2017-099 | 03 - Spearville | 143242 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Current Study | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | 8752548.3451 | 32.03% | 27323646 | 0.3859
GEN-2017-099 | 03 - Spearville | 133079 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 7540554.5 | 100% | 7540554.5 | 1
GEN-2017-099 | 03 - Spearville | 133078 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 527383.5 | 100% | 527383.5 | 1
GEN-2017-100 | 02 - Hitchland | 143693 | ERIS | Beaver County to Woodward 345kV New Line (DISIS-2017-001) | Current Study | Build approximately 60 miles of new 345kV line from Beaver County to Woodward | 65684600.5778 | 50.53% | 130000000 | 0.5038
GEN-2017-100 | 02 - Hitchland | 133081 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | 17186637 | 100% | 17186637 | 1
GEN-2017-100 | 02 - Hitchland | 133080 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | 781840 | 100% | 781840 | 1
Total | [6 empty] | 998058145.75 |  | 3463610988.15

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Granite Falls to Appledorn 230kV Rebuild (DISIS-2017-001) | 144270 | Rebuild the existing Granite Falls to Appledorn 230kV 19.24 mile line to achieve a minimum summer/emergency rating of 430 MVA | WAPA | 36 | 16998713.2
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | St. Joe to Nashua 345kV Rebuild (DISIS-2017-001) (KCPL) | 144268 | Rebuild the existing St. Joe to Nashua 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1335 MVA | Evergy | 36 | 44175538.4
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (GMO) | 143266 | Rebuild the existing St. Joe to Cooper 345kV 38 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | GMO | 36 | 43488872
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (MEC) | 143301 | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 3.34 mile line to achieve a minimum winter/emergency rating of 990 MVA | MEC | 36 | 5158606
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Mission to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | 143316 | Rebuild the existing Mission to Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 95 MVA | WAPA | 36 | 590000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Vetal Tap Terminal Upgrades for Mission Rebuild (DISIS-2017-001) (BEPC) | 143315 | Upgrade terminal equipment at Vetal Tap 115kV 37.87 mile line to achieve a minimum summer/normal rating of 95 MVA | WAPA | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Phillip to Wanblee 115kV Rebuild (DISIS-2017-001) | 144271 | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/normal rating of 125 MVA | WAPA | 36 | 18400000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | ALXNDR to NESCTY 115kV Rebuild (DISIS-2017-001) | 144272 | Rebuild the existing ALXNDR to NESCTY 115kV 18.03 mile line to achieve a minimum winter/emergency rating of 110 MVA | MIDW | 36 | 12816445.2
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sidney_MB3 345kV New Transformer (DISIS-2017-001) | 144274 | Replace the existing Sidney_MB3 345/230kV transformer to achieve a minimum summer/normal rating of 515 MVA | WAPA | 36 | 8302968
Current Study | 15NR | DISIS-2017-001-P2 | NRIS | Sioux City 230 kV Substation Upgrade (DISIS-2017-001) | 144297 | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum winter/emergency rating of 430 MVA | WAPA | 36 | 6000000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Neodesha Jct. 69kV Terminal Upgrades (DISIS-2017-001) | 143296 | Upgrade terminal equipment at Neodesha Jct. to achieve a minimum summer/emergency rating of 40 MVA | Evergy | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Vetal Tap Terminal Upgrades for Martin Rebuild (DISIS-2017-001) (BEPC) | 143305 | Upgrade terminal equipment at Vetal Tap 115kV to achieve a minimum summer/emergency rating of 95 MVA | BEPC | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | St. Joe 345kV Terminal Upgrades for Nashua Rebuild (DISIS-2017-001) (GMO) | 143269 | Upgrade terminal equipment at St. Joe 345kV to achieve a minimum winter/emergency rating of 1335 MVA | GMO | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | St. Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | 144265 | Rebuild the existing St. Joe to Cooper 345kV 26.61 mile line section to achieve a minimum winter/emergency rating of 1245 MVA | OPPD | 36 | 30453654.8
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Cooper 345kV Terminal Upgrades (DISIS-2017-001) | 144267 | Upgrade terminal equipment at Cooper 345kV to achieve a minimum winter/emergency rating of 1245 MVA | NPPD | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sidney_TS4 230kV Terminal Upgrades (DISIS-2017-001) (BEPC) | 143260 | Upgrade terminal equipment at Sidney_TS4 230kV to achieve a minimum summer emergency rating of 510 MVA | BEPC | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (BEPC) | 143261 | Rebuild the existing .65 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | BEPC | 36 | 574280.85
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (LES) | 143262 | Rebuild the existing 1.35 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | LES | 36 | 1192737.15
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sidney_TS4 to Sidney_MB4 Rebuild (DISIS-2017-001) (MRES) | 144263 | Rebuild the existing 2.0 mile 230kV line section from Sidney to Sidney to achieve a minimum summer rating of 510 MVA | MRES | 36 | 1767018
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sidney_MB4 Terminal Upgrades (DISIS-2017-001) (BEPC) | 144264 | Upgrade terminal equipment at Sidney_MB4 230kV to achieve a minimum summer emergency rating of 510 MVA | BEPC | 0 | 0
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Altoona 69kV Terminal Upgrades (DISIS-2017-001) | 143295 | Upgrade terminal equipment at Altoona to Neodesha Jct. to achieve a minimum summer/emergency rating of 40 MVA | Evergy | 36 | 3325
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Appledorn to Watertown 230kV Rebuild (DISIS-2017-001) | 143309 | Rebuild the existing Watertown to Appledorn 230kV 55.3 mile line to achieve a minimum summer/emergency rating of 450 MVA | WAPA | 36 | 10000000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Sarpy Co. S3456 to Council Bluffs 345kV Rebuild (DISIS-2017-001) (OPPD) | 143300 | Rebuild the existing Sarpy Co S3456 to Council Bluffs 345kV 5.63 mile line section to achieve a minimum winter/emergency rating of 990 MVA | OPPD | 36 | 2510992
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Fort Thompson to Fort Randall 230kV Rebuild (DISIS-2017-001) | 143306 | Rebuild the existing Fort Thompson to Fort Randall 87.32 mile line to achieve a minimum summer/emergency rating of 340 MVA | WAPA | 36 | 23568000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Fort Randall to Lake Platte 230kV Rebuild (DISIS-2017-001) (WAPA) | 143307 | Rebuild the existing Fort Randall to Lake Platte 43.34 mile line to achieve a minimum summer/emergency rating of 330 MVA | WAPA | 36 | 2000000
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Martin to Vetal Tap 115kV Rebuild (DISIS-2017-001) (WAPA) | 143304 | Rebuild the existing Martin to Vetal Tap 115kV 16.67 mile line to achieve a minimum summer/emergency rating of 95 MVA | WAPA | 36 | 174097
Current Study | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Beaver County to Woodward 345kV New Line (DISIS-2017-001) | 143693 | Build approximately 60 miles of new 345kV line from Beaver County to Woodward | OGE | 36 | 130000000
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney 345kV Reactive Support (DISIS-2017-001) | 143263 | Install +200 MVAR Capacitor Bank(s) at Finney 345kV | SPS | 18 | 12734040
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001) | 143228 | Rebuild the existing Finney to G17-032 Tap 345kV 78.75 mile line to achieve a minimum Summer/Emergency rating of 425 MVA | SPS | 36 | 150000
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | 143240 | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA | MIDW | 36 | 16500000
Current Study | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | 143242 | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA | Evergy | 36 | 27323646
Contingent | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | GEN-2015-093 Circuit Breaker Addition to Gracemont 138kV substation | 82127 | GEN-2015-093 to add a circuit breaker to the Gracemont 138kV substation as an interconnection upgrade. | OGE | 0 | 1145042
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | 143265 | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 250 MVA | AEP | 36 | 2500000
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (SWPA) | 143264 | Rebuild the existing Beaver to Eureka 161kV 6 mile line section to achieve a minimum light/emergency rating of 250 MVA | SWPA | 36 | 5869344
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Hoyt - JEC 345kV Rebuild (DISIS-2017-001) | 122705 | Rebuild the existing JEC - Hoyt 345 kV line as double circuit 345 kV with normal/minimal emergency rating of 1792 MVA. | Evergy | 48 | 53508060
Current Study | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Mullin Creek to St. Joe 345kV New Line (DISIS-2017-001) (GMO) | 143699 | Build approximately 27 miles of new 345kV line from Mullin Creek to St. Joe | GMO | 36 | 102826609
Current Study | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Mullin Creek 345kV Terminal Upgrades (DISIS-2017-001) (TMO) | 143731 | Upgrade terminal equipment at Mullin Creek 345kV to accept Mullin Creek to St. Joseph new line | TMO | 36 | 7665143
Current Study | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | 143243 | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 295 MVA | WFEC | 36 | 1490000
Current Study | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | 143226 | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | BEPC | 36 | 5906325
Current Study | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Rebuild Ogalala to Sidney 230 kV Line (DISIS-2017-001) | 144275 | Rebuild the existing Ogalala to Sidney 230kV 68.85 mile line to achieve a minimum summer rating of 400 MVA | NPPD | 36 | 60829594.65
Current Study | 00NR | DISIS-2017-001-P2 | NRIS | Antelope to Holt County 345kV New Line (DISIS-2017-001) (NPPD) | 122699 | Build approximately 20 miles of new 345kV line from Antelope to Holt County | NPPD | 36 | 70000000
Contingent | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Multi - Border - Woodward 345 kV Tap NTC 210575/210587 | NTC 2010575/210587 | Tap Woodward to Border approximately 19 miles from Border. Hairpin both lines into Chisholm 345 kV. Include 50 MVAR reactor at Chisholm 345kV. | AEP/OGE | 20 | 24360634
Contingent | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Border 345kV Reactive Support NTC 210609 | NTC 2010609 | Add 275 MVAR of reactive support at Border 345 kV | AEP | 18 | 3996000
Contingent | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Wolf Creek to Blackberry 345kV | 122598 | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | Evergy | 60 | 142601178
Contingent | 17 - Western South Dakota/15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | NTC 200220 (Rplan) | NTC 200220 | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | NPPD | 28 | 412074343
Contingent | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Neset - Northshore 230 kV Ckt 1 NTC 210560 | NTC 210560 | Build new 28 mile 230kV line from Neset to Northshore. | BEPC | 15 | 33155575
Contingent | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Leland Olds 345 kV Substation Reconfiguration (DISIS-2016-002-2) | 122669 | Construct one (1) new 345 kV breaker | BEPC | 15 | 4600000
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (Non-Shared NU) (WAPA) | 133023 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | WAPA | 36 | 7102723
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (TOIF) (WAPA) | 133022 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | WAPA | 36 | 311770
Interconnection | 01 - Woodward | DISIS-2017-001-P2 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (Non-Shared NU) (OKGE) | 132951 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | OGE | 4 | 15000
Interconnection | 01 - Woodward | DISIS-2017-001-P2 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (TOIF) (OKGE) | 132950 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | OGE | 0 | 0
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (Non-Shared NU) (SWPS) | 132997 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | SPS | 36 | 13148764
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (TOIF) (SWPS) | 132996 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | SPS | 36 | 759404
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (Non-Shared NU) (SWPS) | 133081 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | SPS | 36 | 17186637
Interconnection | 02 - Hitchland | DISIS-2017-001-P2 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (TOIF) (SWPS) | 133080 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | SPS | 36 | 781840
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (Non-Shared NU) (ITCGP) | 132963 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 7540554.5
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (TOIF) (ITCGP) | 132962 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 527383.5
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (Non-Shared NU) (ITCGP) | 133079 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 7540554.5
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (TOIF) (ITCGP) | 133078 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | 36 | 527383.5
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (Non-Shared NU) (SWPS) | 132981 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | SPS | 36 | 12750261
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (TOIF) (SWPS) | 132980 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | SPS | 36 | 1708037
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (ITCGP) | 132961 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | ITCGP | 36 | 1412092
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (OKGE) | 143117 | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | OGE | 6 | 30000
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (WERE) | 143118 | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | Evergy | 36 | 13299
Interconnection | 03 - Spearville | DISIS-2017-001-P2 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (TOIF) (ITCGP) | 132960 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | ITCGP | 36 | 918132
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | 132937 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | ITCGP | 36 | 15081109
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | 132936 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | ITCGP | 36 | 1054767
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | 132955 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | SUNC | 30 | 3269931
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P2 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | 132954 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | SUNC | 30 | 2447857
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (Non-Shared NU) (AEPW) | 132983 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEP | 36 | 3877147.5
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P2 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (TOIF) (AEPW) | 132982 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEP | 36 | 1373275
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | 132903 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | AEP | 36 | 20639740
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | 143127 | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | OGE | 10 | 15000
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | 132902 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | AEP | 36 | 1146800
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | 132985 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | AEP | 36 | 8198087
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P2 | ERIS | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | 132984 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | AEP | 36 | 1337068
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (Non-Shared NU) (WERE) | 132939 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | Evergy | 36 | 11434328
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (TOIF) (WERE) | 132938 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | Evergy | 36 | 1216477
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (Non-Shared NU) (WERE) | 132965 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | Evergy | 36 | 4790295
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (TOIF) (WERE) | 132964 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | Evergy | 36 | 696118
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (Non-Shared NU) (OKGE) | 132993 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | OGE | 18 | 5741321
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (TOIF) (OKGE) | 132992 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | OGE | 18 | 599979
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (Non-Shared NU) (OKGE) | 133073 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | OGE | 18 | 5741321
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (TOIF) (OKGE) | 133072 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | OGE | 18 | 599979
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (Non-Shared NU) (GRDA) | 133039 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | GRDA | 18 | 50000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (TOIF) (GRDA) | 133038 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | GRDA | 18 | 1103400
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (Non-Shared NU) (AEPW) | 133047 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | AEP | 36 | 10334726
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (TOIF) (AEPW) | 133046 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | AEP | 36 | 1146800
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (Non-Shared NU) (GRDA) | 133021 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | GRDA | 0 | 0
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (TOIF) (GRDA) | 133020 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | GRDA | 18 | 4548000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (Non-Shared NU) (OKGE) | 133035 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 1721000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (TOIF) (OKGE) | 133034 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 515000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (Non-Shared NU) (OKGE) | 133037 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 1721000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (TOIF) (OKGE) | 133036 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OGE | 15 | 515000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (Non-Shared NU) (WERE) | 132947 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | Evergy | 36 | 15017048
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (TOIF) (WERE) | 132946 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | Evergy | 36 | 1311181
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (Non-Shared NU) (AEPW) | 133041 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | AEP | 30 | 1365027
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (TOIF) (AEPW) | 133040 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | AEP | 30 | 1146800
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (OKGE) | 143125 | Potential interconnection impacts from the following generating facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | OGE | 4 | 20000
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (WERE) | 133065 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | Evergy | 36 | 38569
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (TOIF) (WERE) | 133064 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | Evergy | 0 | 0
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Gordon Evans 138 kV Substation GEN-2017-068 Interconnection (Non-Shared NU) (WERE) | 133031 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Gordon Evans 138 kV Substation. | Evergy | 36 | 1029997
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P2 | ERIS | Gordon Evans 138 kV Substation GEN-2017-068 Interconnection (TOIF) (WERE) | 133030 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Gordon Evans 138 kV Substation. | Evergy | 36 | 657422
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | 133063 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | NPPD | 0 | 0
Interconnection | 09 - Nebraska | DISIS-2017-001-P2 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | 133062 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | NPPD | 0 | 0
Interconnection | 10 - Southeast Oklahoma/Northeast Texas | DISIS-2017-001-P2 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (Non-Shared NU) (AEPW) | 133013 | Rebuild Hosston 69kV as a five (5) breaker ring bus to include control panels, line relaying, disconnect switches, structures, foundations, conductors, insulators, and all other associated work and materials. | AEP | 24 | 17635037
Interconnection | 10 - Southeast Oklahoma/Northeast Texas | DISIS-2017-001-P2 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (TOIF) (AEPW) | 133012 | Construct one (1) 69 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility | AEP | 24 | 1086124
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (Non-Shared NU) (AEPW) | 133045 | Construct one (1) new 345kV breaker, control panels, line relaying, disconnect switches, structures, foundations, conductors, insulators, and all other associated work and materials. | AEP | 24 | 1419431
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (TOIF) (AEPW) | 133044 | Construct one (1) 161 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility. | AEP | 24 | 1125771
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (Non-Shared NU) (EDE) | 133019 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | EMDE | 0 | 0
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (TOIF) (EDE) | 133018 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | EMDE | 0 | 0
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (EDE) | 133057 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | EMDE | 0 | 0
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (WERE) | 143123 | Potential interconnection impacts from the following generating facility, GEN-2017-082 (149.4 MW/Wind), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | Evergy | 36 | 6649
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P2 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (TOIF) (EDE) | 133056 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | EMDE | 0 | 0
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (Non-Shared NU) (KCPL) | 133069 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | Evergy | 36 | 10177602
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P2 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (TOIF) (KCPL) | 133068 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | Evergy | 36 | 824356
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (Non-Shared NU) (OKGE) | 133043 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | OGE | 14 | 1430000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (TOIF) (OKGE) | 133042 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | OGE | 14 | 915000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (Non-Shared NU) (WFEC) | 132967 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | WFEC | 0 | 0
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (TOIF) (WFEC) | 132966 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | WFEC | 36 | 750000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (Non-Shared NU) (OKGE) | 132973 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | OGE | 14 | 1396000
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P2 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (TOIF) (OKGE) | 132972 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | OGE | 14 | 515000
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (Non-Shared NU) (WAPA) | 122574 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | WAPA | 36 | 9000000
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P2 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (TOIF) (WAPA) | 122573 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | WAPA | 36 | 250000
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | 132999 | Construct one (1) 230kV breaker, one (1) 230kV breaker disconnect switch, one (1) set of line PT, one (1) set of CTs, one (1) set of line surge arrestors and all other associated work and materials. | BEPC | 15 | 1296018
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | 132998 | Construct one (1) 230 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility. | BEPC | 15 | 1683828
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | 132949 | Construct one (1) 230kV breaker, one (1) 230kV breaker disconnect switch, one (1) set of line PTs, one (1) set of CTs, one (1) set of line surge arrestors and all other associated work and materials. | BEPC | 15 | 1122522
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P2 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | 132948 | Construct one (1) 230 kV line terminal, line switches, dead end structure, line relaying, communications, revenue metering, line arrestor, and all associated equipment and facilities necessary to accept transmission line from Interconnection Customer’s Generating Facility. | BEPC | 15 | 1674744
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Philip Tap 230 kV GEN-2017-014 Interconnection (Non-Shared NU) (WAPA) | 132957 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Philip Tap 230 kV. | WAPA | 36 | 8500000
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Philip Tap 230 kV GEN-2017-014 Interconnection (TOIF) (WAPA) | 132956 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Philip Tap 230 kV. | WAPA | 36 | 0
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (Non-Shared NU) (WAPA) | 133077 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | WAPA | 0 | 0
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | GEN-2017-014 230kV Reactive Support (DISIS-2017-001) | N/A | Stability identified need to install 30 MVar SVC for Dynamic Reactive Support at GEN-2017-014 230kV Side of Main Transformer | Interconnection Customer | 36 | 6788460
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P2 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (TOIF) (WAPA) | 133076 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | WAPA | 36 | 1208190
1619990917.75

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | " | Non-Converge |  |  | 0.04563 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | " | Non-Converge |  |  | 0.04563 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | " | Non-Converge |  |  | 0.04563 |  | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | " | Non-Converge |  |  | 0.05497 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | " | Non-Converge |  |  | 0.05497 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-013 | " | Non-Converge |  |  | 0.05497 |  | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Non-Converge | 00NR | 0 | 20SP | GEN-2017-014 | " | Non-Converge |  |  | 0.03759 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-014 | " | Non-Converge |  |  | 0.03759 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-014 | " | Non-Converge |  |  | 0.03759 |  | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04742 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04742 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04742 |  | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | " | Non-Converge |  |  | 0.1076 |  | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | " | Non-Converge |  |  | 0.1076 |  | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2017-064 | " | Non-Converge |  |  | 0.1076 |  | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Non-Converge | 00NR | 0 | 24SP | GEN-2017-094 | " | Non-Converge |  |  | 0.06612 |  | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Non-Converge | 00NR | 0 | 24SP | GEN-2017-094 | " | Non-Converge |  |  | 0.06234 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 00NR | 0 | 24SP | GEN-2017-094 | " | Non-Converge |  |  | 0.06234 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 00NR | 0 | 24SP | GEN-2017-014 | " | Non-Converge |  |  | 0.04766 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 00NR | 0 | 24SP | GEN-2017-014 | " | Non-Converge |  |  | 0.04766 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 00NR | 0 | 24SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04592 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 00NR | 0 | 24SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04592 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 00NR | 0 | 24SP | GEN-2017-094 | " | Non-Converge |  |  | 0.06234 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 00NR | 0 | 24SP | GEN-2017-094 | " | Non-Converge |  |  | 0.06234 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 00NR | 0 | 24SP | GEN-2017-014 | " | Non-Converge |  |  | 0.04766 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 00NR | 0 | 24SP | GEN-2017-014 | " | Non-Converge |  |  | 0.04766 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 00NR | 0 | 24SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04592 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 00NR | 0 | 24SP | GEN-2017-064 | " | Non-Converge |  |  | 0.04592 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 |  | 956 | 0.0302 | 101.89 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 |  | 956 | 0.0302 | 101.89 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 |  | 956 | 0.0302 | 101.89 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 |  | 956 | 0.03023 | 101.37 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05662 | 99.8 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-047 | 'FROM -> TO' | 523186 SPEARMAN 3 115 523195 HANSFORD 3 115 1 |  | 159.4 | 0.03252 | 106.41 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-100 | 'FROM -> TO' | 523186 SPEARMAN 3 115 523195 HANSFORD 3 115 1 |  | 159.4 | 0.1545 | 106.41 | P42:345:SPS:POTTERCO:2R05_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-047 | 'FROM -> TO' | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 |  | 318.7 | 0.05483 | 100.88 | P12:115:SPS:V24.1.WOLFTH.TERRY
Thermal | 00NR | 2 | 29SP | GEN-2017-100 | 'FROM -> TO' | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 |  | 318.7 | 0.05533 | 100.88 | P12:115:SPS:V24.1.WOLFTH.TERRY
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.05595 | 122.3 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 19WP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.04604 | 116.01 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 20SP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.04874 | 107.67 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 20SP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.0382 | 106.42 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24SP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.04695 | 108.66 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 24SP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.037 | 106.6 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.05407 | 133.79 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.04474 | 126.56 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 29SP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.05002 | 119.1 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 29SP | GEN-2017-013 | 'FROM -> TO' | 530606 ALXNDR 3 115 530607 NESCTY 3 115 1 |  | 80 | 0.04058 | 114.91 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08086 | 99.79 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08072 | 104.84 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08061 | 102.62 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 533673 ALTOO E2 69.0 533700 NEODJCT2 69.0 1 |  | 36 | 0.08036 | 109.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.03948 | 111.42 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.04502 | 106.16 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.04502 | 106.13 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.04502 | 106.08 | P23:161-345:GMO:EASTOWNE_R7-11::EASTOWNE-IATAN-EASTNT11
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.02996 | 100.7 | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.02996 | 100.5 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.03828 | 109.57 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 00NR | 2 | 29SP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04409 | 104.05 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1
Thermal | 00NR | 2 | 29SP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04409 | 104.05 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN
Thermal | 00NR | 2 | 29SP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04409 | 104 | P23:161-345:GMO:EASTOWNE_R7-11::EASTOWNE-IATAN-EASTNT11
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0497 | 106.16 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0497 | 106.13 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.0497 | 106.08 | P23:161-345:GMO:EASTOWNE_R7-11::EASTOWNE-IATAN-EASTNT11
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.03075 | 111.42 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05139 | 106.16 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05139 | 106.13 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1195 | 0.05139 | 106.08 | P23:161-345:GMO:EASTOWNE_R7-11::EASTOWNE-IATAN-EASTNT11
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04634 | 104.19 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04634 | 104.13 | P23:161-345:GMO:EASTOWNE_R7-11::EASTOWNE-IATAN-EASTNT11
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04634 | 104.13 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.02984 | 109.64 | P23:345:KCPL-GMO:IATAN_R7-9::IATAN-NASHUA-EASTOWNE
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04796 | 104.19 | P23:161-345:GMO:EASTOWNE_R11-14::EASTOWNE-STJOE-EASTNT1
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04796 | 104.13 | P23:161-345:GMO:EASTOWNE_R7-11::EASTOWNE-IATAN-EASTNT11
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 |  | 1136 | 0.04796 | 104.13 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN
Thermal | 00NR | 2 | 24WP | GEN-2017-013 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 |  | 1195 | 0.04024 | 104.18 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 |  | 1195 | 0.03083 | 104.18 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 541199 ST JOE 3 345 640139 COOPER 3 345 1 |  | 1195 | 0.03632 | 104.18 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.24 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.05 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.03 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.24 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 183.96 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 160 |  | 1 | 101.59 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 160 |  | 1 | 101.89 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 160 |  | 1 | 101.94 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 160 |  | 1 | 101.59 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 160 |  | 1 | 102.09 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 631138 LAKEFLD3 345 635368 OBRIEN 3 345 1 |  | 956 | 0.03034 | 106.36 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 635000 CBLUFFS3 345 645456 S3456 3 345 1 |  | 956 | 0.03892 | 103.42 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 640183 GENTLMN3 345 997404 GGS T1 230 1 |  | 336 | 0.06356 | 103.3 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640183 GENTLMN3 345 997404 GGS T1 230 1 |  | 336 | 0.16737 | 103.3 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 640183 GENTLMN3 345 997404 GGS T1 230 1 |  | 336 | 0.06517 | 126.51 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 640183 GENTLMN3 345 997404 GGS T1 230 1 |  | 336 | 0.16898 | 126.51 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 640183 GENTLMN3 345 997408 GGS T1 230 1 |  | 336 | 0.06395 | 111.8 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 640183 GENTLMN3 345 997408 GGS T1 230 1 |  | 336 | 0.15975 | 111.8 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 640184 GENTLMN4 230 997404 GGS T1 230 1 |  | 336 | 0.06356 | 102.51 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640184 GENTLMN4 230 997404 GGS T1 230 1 |  | 336 | 0.16737 | 102.51 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 640184 GENTLMN4 230 997404 GGS T1 230 1 |  | 336 | 0.06517 | 126.24 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 640184 GENTLMN4 230 997404 GGS T1 230 1 |  | 336 | 0.16898 | 126.24 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 640184 GENTLMN4 230 997408 GGS T1 230 1 |  | 336 | 0.06395 | 111.07 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 640184 GENTLMN4 230 997408 GGS T1 230 1 |  | 336 | 0.15975 | 111.07 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.0341 | 104.92 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.03469 | 111.8 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03404 | 121 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03524 | 116.15 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03357 | 113.64 | P24:500:MP:FBS:601LX
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0357 | 112.94 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03329 | 112.63 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03359 | 112.46 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03359 | 112.46 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03329 | 112.38 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03329 | 112.38 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03329 | 112.37 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03329 | 111.79 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03329 | 111.79 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03359 | 111.45 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03359 | 111.45 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03584 | 110.75 | P23:345:XEL:196 BKR SPK AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03583 | 110.75 | P23:345:XEL:192 BKR SPK AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03572 | 110.74 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03572 | 110.74 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03566 | 110.68 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04255 | 110.18 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04234 | 110.16 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0335 | 110.15 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03353 | 109.86 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03353 | 109.86 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03344 | 109.57 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03327 | 109.44 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03327 | 109.43 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03327 | 109.42 | P23:345:OTP:CENTER 3:3235
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03327 | 109.42 | P23:345:OTP:CENTER 3:3245
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03327 | 109.33 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03327 | 109.33 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03665 | 109.21 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03359 | 108.93 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 108.86 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 108.86 | P23:345:XEL:8X25 NOB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 108.86 | P23:345:XEL:8X24 NOB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 108.83 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 108.83 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 108.82 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03701 | 108.8 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03701 | 108.73 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03366 | 108.73 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03492 | 108.65 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03492 | 108.65 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.61 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.61 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0339 | 108.46 | P23:345:MPC:CENTER 3:8810
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0339 | 108.46 | P23:345:MPC:CENTER 3:8820
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.34 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.34 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.34 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.33 | P23:345:MPC:PRAIRIE3:4470
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.32 | P23:345:MPC:PRAIRIE3:4450
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03391 | 108.32 | P23:345:MPC:PRAIRIE3:4440
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03479 | 108.04 | P42:345:NPPD:BKR-HOS-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03319 | 107.97 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 107.94 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.93 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.93 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.93 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.93 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.93 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.93 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.92 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.92 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.92 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.92 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 107.92 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 107.81 | P23:345:XEL:8P6 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 107.8 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03362 | 107.76 | P12:230:XEL-MH:AUTO-SINGLE:PEACEGARD5:GLENBOR4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 107.7 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.58 | P23:345:XEL:8P5 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.53 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.53 | P12:345:XEL:ASAK-ECL SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.52 | P12:345:XEL:ASK-ECL SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.52 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.52 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.52 | P24:345:XEL:8E7 ECL BS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03366 | 107.51 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03366 | 107.51 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03564 | 107.41 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03217 | 107.36 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03217 | 107.36 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03217 | 107.36 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03565 | 107.33 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03565 | 107.33 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 107.32 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 107.32 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03565 | 107.31 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03565 | 107.31 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03258 | 107.28 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03373 | 107.26 | P42:345:NPPD:BKR-SW-3308
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03562 | 107.24 | P23:345:XEL:492 BKR SPK AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03234 | 107.24 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03452 | 107.23 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 107.22 | P12:345:XEL:ASAK-ECL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03431 | 107.13 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03373 | 107.11 | P42:345:NPPD:BKR-SW-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03398 | 107.08 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03376 | 107.03 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04126 | 106.99 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03373 | 106.98 | P12:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03373 | 106.98 | P21:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03372 | 106.98 | P23:345:XEL:8N46 QRY
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04126 | 106.94 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03503 | 106.82 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03779 | 106.79 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03779 | 106.78 | P12:345:UMZ:# 5869 #: IN . PROPER N-1 (LINE) FOR 652529-652829-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03779 | 106.78 | P12:345:UMZW:# 1682 #: WT2 IN SD. WT2-WHT LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.77 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03458 | 106.76 | P12:230:XEL:MNV-GRA-PTH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.76 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03779 | 106.74 | P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION WO A FAULT (WT2-WT2LNX3 LINE REACTOR)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 106.73 | P23:345:XEL:8E5 ECL BS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.7 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03503 | 106.66 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03376 | 106.64 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03405 | 106.61 | P12:230:OTP::HANKSON4:OAKES 4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 106.59 | P12:230:OTP:AUTO-SINGLE:WAHPETN4:FERGSFL4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03404 | 106.59 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.54 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.54 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.54 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.53 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.52 | P55:345:ATC:ARPIN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 106.49 | P11:115:UMZZ:# 2991 #: BH IN SD. LOSS OF BEETHOVEN WIND FARM
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.47 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.47 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03466 | 106.42 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03425 | 106.41 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03425 | 106.41 | P12:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.4 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03404 | 106.33 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.33 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:GRE-HENNING4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03433 | 106.29 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0354 | 106.28 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0354 | 106.28 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03294 | 106.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03432 | 106.27 | P12:230:XEL:AUTO-SINGLE:MNVLTAP4:GRE-PANTHER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.26 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03526 | 106.26 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.25 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.25 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.25 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 106.25 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0354 | 106.25 | P23:345:WAPA:SIOUXCY:8692
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0338 | 106.25 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0338 | 106.25 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.034 | 106.23 | P42:345:NPPD:BKR-GGS-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 106.22 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 106.22 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 106.21 | P12:230:OTP-GRE::GRE-SILVRLK4B2.SLV-INM
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0343 | 106.16 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03342 | 106.14 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03342 | 106.14 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03395 | 106.1 | P12:230:OTP:AUTO-SINGLE:WILTON4:WINGER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03451 | 106.06 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03415 | 106.04 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0339 | 105.96 | P23:345:XEL:8N5 MNN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.93 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.93 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03409 | 105.92 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.9 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.9 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.9 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 105.88 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 105.88 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03402 | 105.86 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03402 | 105.86 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03392 | 105.86 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03392 | 105.86 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.77 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03416 | 105.77 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.73 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.73 | P23:345:MEC:CBEC 908
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 105.72 | P23:345:ALTW:MITCHLCO:1160
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03708 | 105.72 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.71 | P11:345:UMZB:# 15 #: LO IN ND. LELAND OLDS 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.7 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.68 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.68 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.68 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.66 | P13:230:MDU:TATANKA GSU & COLLECTOR LOSS:TATANKA::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.66 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 105.65 | P23:345:MEC:CBEC 905
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.59 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03402 | 105.57 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.57 | P13:014-115:GRIS:GSUPGS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.57 | P11:115:GRIS:PGS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03389 | 105.44 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.41 | P23:345:XEL:8N8 MNN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.4 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.4 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.4 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.4 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.4 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03403 | 105.39 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03403 | 105.39 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03403 | 105.39 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.37 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.35 | P11:345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.35 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.35 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.35 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.34 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.32 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.32 | P11:345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.32 | P13:18-345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.32 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.31 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.29 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.29 | P11:115:XEL:HBR #6 7 8
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.29 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.29 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.29 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.26 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.26 | P13:23-345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.26 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.26 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.25 | P11:115:UMZB:# 34 #: PWN IN ND. NDPRARIE WINDS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.24 | P12:116:UMZB:# 2911 #: LND IN ND. LINDAHL - NESET
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.24 | P12:115:UMZ:# 5700 #: IN . PROPER N-1 (LINE) FOR 655946-655947-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.22 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.19 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.19 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.18 | P11:22:AEPW:NES3-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.18 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.18 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 105.18 | P11:230:MDU::TATANKA::W::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.14 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.14 | P11:22:AEPW:FLINTCR1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.14 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.14 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.14 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.14 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.13 | P11:035:UMZW:# 28 #: WWC IN SD. LOSS OF UNIT (WIND).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.13 | P12:HV:EES::FLINTCR5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.13 | P13:161-22:AEPW:FLINTCR5
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.13 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.12 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.12 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.11 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.11 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.1 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.1 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.1 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.1 | P23:345:XEL:8P1 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.09 | P11:115:XEL:HBR #6
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.09 | P11:115:XEL:HBR #7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 105.09 | P12:115:UMZ:# 5537 #: IN . PROPER N-1 (LINE) FOR 652421-659262-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P11:014:UMZB:# 41 #: WILT3 IN ND. WILTON 3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P11:15:XEL:AUTO-SINGLE:MEC-CT1:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P11:19:XEL:AUTO-SINGLE:MEC-ST:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P23:345:XEL:8S24 WLM AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P12:115:OTP:AUTO-SINGLE:COURTENAYW7:JAMSTWN7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.08 | P11:22:EES-EAI:ARK_NU:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 105.08 | P12:115:UMZ:# 5798 #: IN . PROPER N-1 (LINE) FOR 659112-659262-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 105.08 | P12:115:UMZB:# 2944 #: CQ IN MT. POPLAR - WILLISTON
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.07 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.07 | P12:EHV:EES::8ANO%:1(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.07 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.07 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.07 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.07 | P12:115:XEL:AUTO-SINGLE:WILMART7:MEC-115:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.06 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.05 | P12:EHV:EES::8ANO%:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.05 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.05 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.05 | P11:115:UMZB:# 2 #: CQ IN ND. CULBERTSON GEN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.04 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.04 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.03 | P11:0:OTP:AUTO-SINGLE:ASH2GEN9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.03 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.03 | P13:230-34:OTP:AUTO-SINGLE:SIBLEY4:ASH39:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.03 | P11:0:OTP:AUTO-SINGLE:ASH3GEN9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.02 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.02 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.01 | P11:18:XEL:AUTO-SINGLE:HBRC71G:7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.01 | P11:18:XEL:AUTO-SINGLE:HBRC72G:8
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.01 | P11:18:XEL:AUTO-SINGLE:COLVILLG:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.01 | P11:18:XEL:AUTO-SINGLE:COLVILL1G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.01 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 105.01 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.99 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.99 | P12:230:OTP:AUTO-SINGLE:BARNES4:SIBLEY4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.99 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P11:014:UMZB:# 39 #: WILT1 IN ND. WILTON 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P11:16:GRE:AUTO-SINGLE:GRE-ER14G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P23:345-161:XEL:ADAMS_I:680_S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P23:345-161:XEL:ADAMS_I:681_S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P41:345:OKGE:SB_SOER7382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.98 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.97 | P11:001:UMZB:# 26 #: WILT2 IN ND. WILTON 2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03487 | 104.97 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.97 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.97 | P11:230:WERE:JECU1_GEN::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.97 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P11:345:WERE:JECU2_GEN::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P23:345:WERE:JEC_345-15::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.96 | P11:115:MDU::HESKETT::3::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P13:115:MDU:HESKETT 3 GSU LOSS:HESKETT::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P11:345:WERE:JECU3_GEN::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P23:345:WERE:JEC_345-19::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P13:230:MDU:THUNDER SPIRIT & G752-2 GSUS & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P13:230:MDU:THUNDER SPIRIT GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.96 | P13:230:MDU:HETTINGER GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.95 | P23:345:WERE:JEC_345-20::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 104.94 | P23:345:XEL:8P2 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.94 | P41:345:OKGE:SB_SEOL7383
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.93 | P41:345:OKGE:SB_SEOL7382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.92 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.92 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.91 | P23:345:WERE:JEC_345-16::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.91 | P11:115:MDU::LEWIS & CLARK::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.88 | P11:230:MDU::THUNDER SPIRIT::W::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.88 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.88 | P11:230:MDU::G752-2::W::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.87 | P12:115:XEL:DLK-HYL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.86 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.85 | P41:345:OKGE:SB_MUGE7384
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.85 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.85 | P12:EHV:EES::MUSKOGE7!:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.84 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.84 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG6G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.84 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.84 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG5G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P11:014:UMZW:# 81 #: OA IN SD. LOSS OF UNIT (6).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P11:014:UMZW:# 80 #: OA IN SD. LOSS OF UNIT (5).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P11:014:UMZW:# 82 #: OA IN SD. LOSS OF UNIT (7).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P11:014:UMZW:# 78 #: OA IN SD. LOSS OF UNIT (3).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P11:014:UMZW:# 77 #: OA IN SD. LOSS OF UNIT (2).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.83 | P11:014:UMZW:# 79 #: OA IN SD. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.82 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.81 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.8 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 104.79 | P13:115-230:NPPD:NUCOR-3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.78 | P11:014:UMZW:# 46 #: BG IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.78 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB19:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.78 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB29:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.78 | P11:0:OTP:AUTO-SINGLE:J262COURTW:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.78 | P11:0:OTP:AUTO-SINGLE:J263COURTW:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.73 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.65 | P12:230:OTP-MPC:B2.PB4-LUV
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.65 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:LUVERNE4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.64 | P13:230-34:OTP:AUTO-SINGLE:LUVERNE4:ASH29:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.6 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.58 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.58 | P11:0:XEL:AUTO-SINGLE:J183PROSEW2:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.58 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.58 | P11:0:XEL:AUTO-SINGLE:J183PROSEW1:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03399 | 104.51 | P13:230-345:NPPD:NUCOR-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.47 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.46 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03421 | 104.45 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.43 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03657 | 104.39 | P12:230:UMZW:# 686 #: FT IN SD. FT-OA4 LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03657 | 104.39 | P12:230:UMZW:# 685 #: FT IN SD. FT-OA3 LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.35 | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 104.35 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 104.35 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 104.35 | P23:345:SUNC:MO_BRK182
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03415 | 104.34 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.34 | P11:18:ITCM:EMERYGT1:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03415 | 104.34 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.34 | P11:18:ITCM:EMERYGT2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03415 | 104.33 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.33 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03414 | 104.32 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.31 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.31 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03419 | 104.31 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.31 | P23:500:EES-EAI:KEO:B4921
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.3 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.3 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.3 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03434 | 104.3 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03434 | 104.3 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.27 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03398 | 104.26 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.26 | P13:34-161:ALTW:AUTO-SINGLE:G735_WF5:CRYSTLKII5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.26 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CRYSTLKII5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.26 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03417 | 104.24 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 104.21 | P23:345:MEC:MADISON CO 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 104.21 | P23:500:EES-EAI:KEO:B4941
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.21 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.2 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.19 | P13:161-69:ITCM:LIME CK5 T1:IA-NW
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.17 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03418 | 104.17 | P42:345:NPPD:BKR-RW-3302
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 104.15 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03757 | 104.14 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03757 | 104.14 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03757 | 104.13 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03757 | 104.13 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03418 | 104.13 | P23:345:SUNC:MO_BRK188
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03418 | 104.13 | P23:345:SUNC:MO_BRK388
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03418 | 104.13 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.11 | P23:345:MEC:HIGHLAND 906
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03751 | 104.11 | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 104.1 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 104.08 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.91 | P13:13-115:GRE-OTP:AUTO-SINGLE:GRE-SPRITWDG:SPIRITWD7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.87 | P11:16:GRE:AUTO-SINGLE:GRE-CGS82G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.85 | P23:345:XEL-SMMPA:8H9 PRI AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03418 | 103.83 | P42:345:NPPD:BKR-AXT-3302
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.83 | P23:345:XEL:8S98 NRH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.81 | P23:345:XEL-SMMPA:8H8 PRI AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03408 | 103.72 | P12:115:GRE:VLT-MCH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.7 | P42:345:NPPD:BKR-MOR-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.68 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.68 | P21:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03416 | 103.67 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03416 | 103.67 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03416 | 103.67 | P23:345:MEC:KOSSUTH 904
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03415 | 103.64 | P42:345:NPPD:BKR-AXT-3308
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.63 | P23:345:GRE:PVS 19JB4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.62 | P23:345:GRE:PVS 19JB1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.59 | P13:230-34:XEL:AUTO-SINGLE:PEACEGARD5:PEACEGARD9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.59 | P11:0:XEL:AUTO-SINGLE:J290BORDRW:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.58 | P23:345:MEC:GDMEC 902
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.58 | P23:345:MEC:GDMEC 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.56 | P12:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.56 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.56 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.56 | P23:345:MEC:BONDURANT 906
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.52 | P23:345:MEC:SYCAMORE 902
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.52 | P42:345:NPPD:BKR-MOR-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.52 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.52 | P23:345:MEC:MONTEZUMA 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.52 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.52 | P23:345:MEC:SYCAMORE 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.47 | P23:345:SMP:BYRON 3-GRE-PL VLLY3 BKR8S16
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.47 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03412 | 103.46 | P24:345:SMP:BYRON 3-BUS TIE BKR8S15
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.4 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.38 | P13:115:MDU:HESKETT 2 GSU LOSS:HESKETT::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.38 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 103.36 | P23:345:MEC:MONTEZUMA 903
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03388 | 103.34 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.28 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.28 | P11:024:DPC:ALMA2:6
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0341 | 103.23 | P11:115:MDU::HESKETT::2::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03413 | 103.22 | P23:345:XEL:8S97 NRH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03411 | 102.97 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0342 | 102.96 | P23:345:XEL:8S72 HNA
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03409 | 102.74 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03409 | 102.74 | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03409 | 102.74 | P12:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03409 | 102.74 | P21:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03374 | 102.36 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03441 | 102.26 | P12:345:MEC:OBRIEN-LAKEFIELD + REACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03441 | 102.26 | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03441 | 102.26 | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03441 | 102.26 | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03408 | 102.25 | P21:345:UMZW:# 325 #: GI IN NE. GI-MCCOOL LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0344 | 102.15 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0344 | 102.15 | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0344 | 102.15 | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0344 | 102.14 | P23:345:MEC:HIGHLAND 902
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0344 | 102.14 | P23:345:MEC:HIGHLAND 903
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03441 | 101.95 | P23:345:MEC:OBRIEN 904
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0345 | 101.41 | P23:345:MEC:OBRIEN 903
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03219 | 101.05 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 130.79 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03589 | 123.02 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03624 | 120.55 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 119.87 | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 119.87 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 119.04 | P12:500:MH:M602F
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 119.04 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 119.04 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 118.72 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 118.72 | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03431 | 118.67 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03431 | 118.67 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 118.52 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03449 | 118.52 | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0343 | 118.46 | P24:500:MP:FBS:601LX
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03631 | 118.44 | P23:345:XEL:192 BKR SPK AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03632 | 118.44 | P23:345:XEL:196 BKR SPK AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03621 | 118.44 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03621 | 118.44 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03622 | 118.08 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03431 | 117.98 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03431 | 117.98 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0432 | 117.83 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04299 | 117.79 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03715 | 117.18 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03757 | 117.16 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03757 | 117.11 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 117.09 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03407 | 117.09 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03404 | 116.76 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03408 | 116.63 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03379 | 116.57 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03379 | 116.56 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03398 | 116.53 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0338 | 116.53 | P23:345:OTP:CENTER 3:3235
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0338 | 116.52 | P23:345:OTP:CENTER 3:3245
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03379 | 116.44 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03379 | 116.44 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03417 | 116.37 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0352 | 115.72 | P23:345:XEL:8X25 NOB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0352 | 115.72 | P23:345:XEL:8X24 NOB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0352 | 115.69 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0352 | 115.69 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0352 | 115.67 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03446 | 115.55 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03446 | 115.55 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.28 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.28 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.28 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.28 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.28 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.28 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.26 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.26 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.26 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.26 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03478 | 115.26 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03618 | 115.24 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03446 | 115.21 | P23:345:MPC:PRAIRIE3:4440
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03446 | 115.18 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03446 | 115.18 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03446 | 115.18 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03619 | 115.16 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03619 | 115.16 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03619 | 115.13 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03619 | 115.13 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03556 | 115.02 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03556 | 115.02 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03616 | 115.01 | P23:345:XEL:492 BKR SPK AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03363 | 115.01 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03421 | 114.53 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03421 | 114.53 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03289 | 114.52 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03427 | 114.48 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03593 | 114.45 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03593 | 114.45 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.43 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03593 | 114.42 | P23:345:WAPA:SIOUXCY:8692
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03547 | 114.42 | P42:345:NPPD:BKR-HOS-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03467 | 114.41 | P23:345:XEL:8P6 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03317 | 114.38 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03272 | 114.37 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03272 | 114.37 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03272 | 114.37 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03456 | 114.34 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03836 | 114.29 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03836 | 114.29 | P12:345:UMZ:# 5869 #: IN . PROPER N-1 (LINE) FOR 652529-652829-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03836 | 114.29 | P12:345:UMZW:# 1682 #: WT2 IN SD. WT2-WHT LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03422 | 114.28 | P42:345:NPPD:BKR-GGS-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03512 | 114.25 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03836 | 114.24 | P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION WO A FAULT (WT2-WT2LNX3 LINE REACTOR)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03538 | 114.22 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 114.18 | P23:345:XEL:8P5 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.13 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.13 | P12:345:XEL:ASAK-ECL SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.12 | P12:345:XEL:ASK-ECL SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.12 | P24:345:XEL:8E7 ECL BS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.12 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 114.11 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03427 | 114.04 | P23:345:XEL:8N46 QRY
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03428 | 114 | P12:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03428 | 114 | P21:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03491 | 113.94 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.9 | P12:345:XEL:ASAK-ECL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.9 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.9 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04199 | 113.86 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0345 | 113.81 | P13:115-230:GRE:RMS TR1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03564 | 113.81 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.04199 | 113.8 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03517 | 113.79 | P12:230:XEL:MNV-GRA-PTH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.78 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 113.68 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03564 | 113.63 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 113.59 | P12:230:OTP::HANKSON4:OAKES 4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03332 | 113.55 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 113.54 | P11:115:UMZZ:# 2991 #: BH IN SD. LOSS OF BEETHOVEN WIND FARM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03521 | 113.5 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03462 | 113.44 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.43 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.39 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.37 | P12:230:OTP:AUTO-SINGLE:WAHPETN4:FERGSFL4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03485 | 113.34 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03485 | 113.34 | P12:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03463 | 113.32 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03389 | 113.31 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03389 | 113.31 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.28 | P23:345:XEL:8E5 ECL BS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03492 | 113.28 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 113.26 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 113.26 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03491 | 113.25 | P12:230:XEL:AUTO-SINGLE:MNVLTAP4:GRE-PANTHER4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.25 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03596 | 113.24 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.24 | P23:345:MEC:BLACK HAWK 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03438 | 113.23 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03438 | 113.23 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 113.21 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 113.21 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.17 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:GRE-HENNING4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 113.13 | P12:230:OTP-GRE::GRE-SILVRLK4B2.SLV-INM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.13 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.13 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.13 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03489 | 113.11 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.1 | P55:345:ATC:ARPIN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 113.1 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0351 | 113.09 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03458 | 113.01 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03457 | 112.97 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03457 | 112.97 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 112.97 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 112.96 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 112.96 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 112.96 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 112.95 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.95 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.87 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0345 | 112.87 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0345 | 112.87 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 112.86 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03447 | 112.86 | P23:345:XEL:8N5 MNN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.83 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.83 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03459 | 112.8 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.77 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.77 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.77 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.77 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.77 | P23:345:MEC:CBEC 908
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.75 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.74 | P23:345:MEC:CBEC 905
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 112.71 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03758 | 112.71 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 112.64 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 112.64 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.64 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.64 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.64 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.61 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 112.59 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03459 | 112.56 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.5 | P13:014-115:GRIS:GSUPGS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.5 | P11:115:GRIS:PGS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.5 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.49 | P11:13:OTP:AUTO-SINGLE:HOOTLK3G:3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03582 | 112.49 | P12:115:UMZZ:# 228 #: MEN IN SD. MENNO JUNCTION IS A TAP (UJ-MEN-TP).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03582 | 112.49 | P12:115:UMZ:# 5614 #: IN . PROPER N-1 (LINE) FOR 652626-660007-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.43 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.43 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.43 | P42:500:OKGE:SB_FTTH8583
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.43 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.43 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03432 | 112.38 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03464 | 112.36 | P23:345:XEL:8M53 SCO
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03464 | 112.36 | P23:345:XEL:8M54 SCO
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03464 | 112.35 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03464 | 112.35 | P21:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.32 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.32 | P11:345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.32 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.31 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.31 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.31 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.31 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.3 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.3 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.3 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.3 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.3 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.29 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.29 | P11:345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.29 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.29 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.29 | P13:18-345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.28 | P13:23-345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.28 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.28 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.26 | P11:115:UMZB:# 36 #: GGS2 IN SD. GROTON 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.26 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03462 | 112.25 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.24 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03462 | 112.23 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03462 | 112.23 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.19 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.19 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.18 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.18 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.18 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.17 | P23:345:XEL:8N8 MNN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.17 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.14 | P12:116:UMZB:# 2911 #: LND IN ND. LINDAHL - NESET
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.14 | P12:115:UMZ:# 5700 #: IN . PROPER N-1 (LINE) FOR 655946-655947-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.14 | P11:115:UMZB:# 34 #: PWN IN ND. NDPRARIE WINDS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112.12 | P11:230:MDU::TATANKA::W::::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.11 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.11 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.1 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.1 | P11:22:AEPW:NES3-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.1 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.1 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.09 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.09 | P11:22:AEPW:RSS2-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.09 | P11:24:AEPW:RSS1-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.08 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.07 | P13:138-22:AEPW:R.S.S.-4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.07 | P13:138-24:AEPW:R.S.S.-4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.07 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.05 | P11:22:AEPW:FLINTCR1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.05 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.05 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.04 | P13:161-22:AEPW:FLINTCR5
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.04 | P11:035:UMZW:# 28 #: WWC IN SD. LOSS OF UNIT (WIND).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.02 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.02 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.01 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.01 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112.01 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112 | P11:22:EES-EAI:ARK_NU:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 112 | P11:15:XEL:AUTO-SINGLE:MEC-CT1:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 112 | P23:345:XEL:8S24 WLM AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03466 | 111.99 | P12:115:UMZ:# 5537 #: IN . PROPER N-1 (LINE) FOR 652421-659262-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.99 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.99 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.99 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.99 | P11:19:XEL:AUTO-SINGLE:MEC-ST:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.99 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.99 | P23:345:XEL:8P1 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.98 | P11:115:UMZB:# 2 #: CQ IN ND. CULBERTSON GEN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.97 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03466 | 111.97 | P12:115:UMZ:# 5798 #: IN . PROPER N-1 (LINE) FOR 659112-659262-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03466 | 111.97 | P12:115:UMZB:# 2944 #: CQ IN MT. POPLAR - WILLISTON
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.97 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.96 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.96 | P12:115:XEL:AUTO-SINGLE:WILMART7:MEC-115:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.96 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.96 | P11:014:UMZB:# 41 #: WILT3 IN ND. WILTON 3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.96 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.96 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.95 | P11:0:OTP:AUTO-SINGLE:ASH2GEN9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.95 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.95 | P11:014:UMZB:# 2987 #: PIONEER RECIP B IN ND. PIONEER RECIP PACK B
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.95 | P11:014:UMZB:# 2986 #: PIONEER RECIP A IN ND. PIONEER RECIP PACK A
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.94 | P11:115:XEL:HBR #7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.94 | P11:115:XEL:HBR #6
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.94 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.93 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.93 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.92 | P11:0:OTP:AUTO-SINGLE:ASH3GEN9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.92 | P12:230:OTP:AUTO-SINGLE:BARNES4:SIBLEY4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.92 | P13:230-34:OTP:AUTO-SINGLE:SIBLEY4:ASH39:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.92 | P23:345:XEL:8P2 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.92 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.91 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.9 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.9 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.9 | P13:115:MDU:HESKETT 3 GSU LOSS:HESKETT::1::::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 111.89 | P11:115:MDU::HESKETT::3::::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P13:138-24:AEPW:TURK 4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P11:24:AEPW:TURKCOAL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P11:18:XEL:AUTO-SINGLE:COLVILLG:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P11:18:XEL:AUTO-SINGLE:COLVILL1G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P11:001:UMZB:# 26 #: WILT2 IN ND. WILTON 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.89 | P11:014:UMZB:# 39 #: WILT1 IN ND. WILTON 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.88 | P11:16:GRE:AUTO-SINGLE:GRE-ER14G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.88 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.88 | P11:18:XEL:AUTO-SINGLE:HBRC72G:8
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.88 | P11:18:XEL:AUTO-SINGLE:HBRC71G:7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.88 | P41:345:OKGE:SB_SOER7382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.88 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.87 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.87 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.87 | P11:115:MDU::LEWIS & CLARK::1::::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.86 | P11:345:OKGE:BKRBKR_GSU27
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.86 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.85 | P41:345:OKGE:SB_REUD7381
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.85 | P41:345:OKGE:SB_REUD7383
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 111.85 | P12:115:UMZ:# 5567 #: IN . PROPER N-1 (LINE) FOR 655490-652525-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 111.85 | P12:115:UMZW:# 509 #: TY IN SD. TY-YJ LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.85 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.85 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.84 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.83 | P41:345:OKGE:SB_SEOL7383
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.82 | P41:345:OKGE:SB_SEOL7382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.82 | P13:115:MDU:LEWIS & CLARK GSU LOSS:LEWIS & CLARK::1::::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.81 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.81 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 111.77 | P12:115:XEL:DLK-HYL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 111.77 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.74 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.73 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.73 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.72 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO28:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.72 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.7 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.7 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.7 | P41:345:OKGE:SB_MUGE7384
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.7 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.69 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.67 | P11:014:UMZW:# 46 #: BG IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 111.61 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.59 | P11:0:OTP:AUTO-SINGLE:J262COURTW:W
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.59 | P11:0:OTP:AUTO-SINGLE:J263COURTW:W
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.59 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB29:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.59 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB19:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03459 | 111.52 | P13:230-345:NPPD:NUCOR-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.52 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:LUVERNE4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.52 | P12:230:OTP-MPC:B2.PB4-LUV
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.51 | P13:230-34:OTP:AUTO-SINGLE:LUVERNE4:ASH29:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.5 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.42 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.42 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.35 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03459 | 111.3 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03726 | 111.28 | P12:230:UMZW:# 684 #: FT IN SD. FT-OA2 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.25 | P11:34:ALTW:AUTO-SINGLE:G735_WF5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03736 | 111.25 | P12:230:UMZW:# 686 #: FT IN SD. FT-OA4 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03736 | 111.25 | P12:230:UMZW:# 685 #: FT IN SD. FT-OA3 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.19 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.16 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 111.14 | P23:345:MEC:MADISON CO 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.14 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.14 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.13 | P11:18:ITCM:EMERYGT1:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.12 | P11:18:ITCM:EMERYGT2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.07 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.07 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.07 | P23:345:XEL:8S22 WLM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 111.07 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.07 | P13:34-161:ALTW:AUTO-SINGLE:G735_WF5:CRYSTLKII5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.06 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.06 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CRYSTLKII5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.04 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.03 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.03 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.03 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.03 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03487 | 111.02 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03487 | 111.02 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 111.02 | P23:345:MEC:HIGHLAND 906
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.01 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 111.01 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.99 | P13:161-69:ITCM:LIME CK5 T1:IA-NW
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.99 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.98 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03832 | 110.97 | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03473 | 110.95 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03487 | 110.95 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03499 | 110.95 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03499 | 110.94 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.93 | P23:345:MEC:GDMEC 902
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.93 | P23:345:MEC:GDMEC 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03499 | 110.92 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 110.91 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03468 | 110.91 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.9 | P23:345:MEC:BONDURANT 906
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03838 | 110.89 | P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03417 | 110.88 | P12:115:NPPD:1090:AINSWND7:THEDFRD7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.86 | P23:345:MEC:SYCAMORE 902
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.86 | P23:345:MEC:MONTEZUMA 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.86 | P23:345:MEC:SYCAMORE 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03437 | 110.84 | P13:115-345:NPPD:THEDFRD3:T2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03486 | 110.81 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.78 | P13:13-115:GRE-OTP:AUTO-SINGLE:GRE-SPRITWDG:SPIRITWD7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.76 | P23:345:XEL-SMMPA:8H9 PRI AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.74 | P23:345:XEL:8S98 NRH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.73 | P23:345:MEC:MONTEZUMA 903
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.0347 | 110.71 | P23:345:XEL-SMMPA:8H8 PRI AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03455 | 110.62 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.59 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.59 | P21:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.57 | P23:345:GRE:PVS 19JB4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.56 | P23:345:GRE:PVS 19JB1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 110.55 | P23:345:SUNC:HLC_BRK282
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.53 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.53 | P12:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03838 | 110.51 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03838 | 110.51 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03838 | 110.5 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03838 | 110.5 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.45 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.38 | P24:345:SMP:BYRON 3-BUS TIE BKR8S15
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.38 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.38 | P23:345:SMP:BYRON 3-GRE-PL VLLY3 BKR8S16
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.36 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.35 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.35 | P23:345:SUNC:MO_BRK182
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.35 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.33 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.33 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 110.31 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03467 | 110.31 | P12:115:GRE:VLT-MCH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03473 | 110.3 | P42:345:NPPD:BKR-SW-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03479 | 110.29 | P23:345:MEC:KOSSUTH 904
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03479 | 110.29 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03479 | 110.29 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03471 | 110.28 | P42:345:NPPD:BKR-MOR-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03472 | 110.23 | P23:345:XEL:8S97 NRH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03476 | 110.21 | P42:345:NPPD:BKR-GGS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03473 | 110.21 | P42:345:NPPD:BKR-MOR-3306
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.19 | P13:230-34:XEL:AUTO-SINGLE:PEACEGARD5:PEACEGARD9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03474 | 110.18 | P42:345:NPPD:BKR-SW-3304
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.1 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03473 | 110.06 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 110.04 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03477 | 109.85 | P42:345:NPPD:BKR-AXT-3302
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03475 | 109.82 | P42:345:NPPD:BKR-AXT-3308
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03497 | 109.81 | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03497 | 109.81 | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03497 | 109.81 | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03443 | 109.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 109.15 | P12:115:NPPD:TSGT3:LAMAR 7:GRANTNB7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03469 | 109.15 | P12:115:TSGT-BEPC_659:::GRANTNB_-TS7-LAMAR___-TS7-1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03716 | 106.34 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.03838 | 101.17 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 131.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 131.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03558 | 110.12 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03558 | 110.12 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03797 | 110.12 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03797 | 110.12 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03057 | 101.02 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03057 | 101.02 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03296 | 101.02 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03296 | 101.02 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03073 | 118.84 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03073 | 118.84 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03312 | 118.84 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03312 | 118.84 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03785 | 131.22 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03785 | 131.22 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.04024 | 131.22 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.04024 | 131.22 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03152 | 113.07 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03152 | 113.07 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0339 | 113.07 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0339 | 113.07 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04916 | 109.29 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04879 | 108.61 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04582 | 107.67 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04627 | 107.17 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04804 | 101.63 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04691 | 101.48 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04612 | 99.87 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04719 | 99.74 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04612 | 99.67 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04612 | 99.67 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04612 | 99.67 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04716 | 99.65 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05369 | 109.29 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05273 | 108.61 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04466 | 107.67 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04525 | 107.17 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05073 | 101.63 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04781 | 101.48 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.0458 | 99.87 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04627 | 99.74 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.0458 | 99.67 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.0458 | 99.67 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.0458 | 99.67 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04626 | 99.65 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04978 | 106.94 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04933 | 106.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04657 | 106.09 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.03063 | 103.57 | P12:115:UMZW:# 144 #: GY-BO-FR IN SD. GY-BO-FR BONESTEEL HAS FAULT INTERUPTING DEVIECES (NOT BREAKERS)
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.03063 | 103.57 | P12:115:UMZ:# 5572 #: IN . PROPER N-1 (LINE) FOR 652475-652478-1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04629 | 101.84 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04529 | 100.71 | P12:115:NPPD:1090:AINSWND7:THEDFRD7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05431 | 106.94 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05314 | 106.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04484 | 106.09 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04471 | 101.84 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652479 MARTIN 7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.046 | 100.71 | P12:115:NPPD:1090:AINSWND7:THEDFRD7:BTB
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04916 | 105.54 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04879 | 104.87 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04582 | 103.96 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04627 | 103.28 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05369 | 105.54 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05273 | 104.87 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04466 | 103.96 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04525 | 103.28 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04978 | 102.99 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04933 | 102.16 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04657 | 101.93 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.03063 | 99.52 | P12:115:UMZ:# 5572 #: IN . PROPER N-1 (LINE) FOR 652475-652478-1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.03063 | 99.52 | P12:115:UMZW:# 144 #: GY-BO-FR IN SD. GY-BO-FR BONESTEEL HAS FAULT INTERUPTING DEVIECES (NOT BREAKERS)
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05431 | 102.99 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.05314 | 102.16 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 652482 MISSION7 115 659153 VETAL_TP-RM7 115 1 |  | 88 | 0.04484 | 101.93 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.0571 | 102.7 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652487 PHILIP 7 115 652579 WANBLEE 7 115 1 |  | 120 | 0.05698 | 100.57 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.05416 | 99.56 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.05379 | 105.87 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.04196 | 99.56 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 |  | 320 | 0.0416 | 105.87 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.05279 | 101.59 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 |  | 320 | 0.04082 | 101.59 | P12:345:UMZ:# 6230 #: OUT-YEAR GRP TO HOLT CO - PROPER N-1 (LINE) FOR 652832-640510-1 OR 652832-652532-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 |  | 352 | 0.03227 | 122.33 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 |  | 352 | 0.03189 | 119.42 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 |  | 352 | 0.0322 | 125.36 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652530 WATERTN4 230 652582 APPLEDORN 4 230 1 |  | 352 | 0.03854 | 100.94 | P12:230:UMZW:# 171 #: WT IN SD. WT-FB LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.0341 | 104.78 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 720 |  | 0.03469 | 111.6 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03404 | 120.66 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03524 | 116.01 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03357 | 113.38 | P24:500:MP:FBS:601LX
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0357 | 112.73 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03329 | 112.38 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03359 | 112.22 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03359 | 112.22 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03329 | 112.13 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03329 | 112.13 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03329 | 112.13 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03329 | 111.56 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03329 | 111.56 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03359 | 111.22 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03359 | 111.22 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03584 | 110.54 | P23:345:XEL:196 BKR SPK AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03583 | 110.54 | P23:345:XEL:192 BKR SPK AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03572 | 110.53 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03572 | 110.53 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03566 | 110.5 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04255 | 109.99 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04234 | 109.96 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0335 | 109.93 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03353 | 109.65 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03353 | 109.65 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03344 | 109.36 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03327 | 109.23 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03327 | 109.22 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03327 | 109.21 | P23:345:OTP:CENTER 3:3235
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03327 | 109.21 | P23:345:OTP:CENTER 3:3245
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03327 | 109.12 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03327 | 109.12 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03665 | 109.04 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03359 | 108.74 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 108.69 | P23:345:XEL:8X25 NOB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 108.69 | P23:345:XEL:8X24 NOB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 108.66 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 108.66 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 108.65 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 108.64 | P11:345:UMZB:# 5 #: DCS IN SD. DEERCREEK
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03701 | 108.59 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03366 | 108.54 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03492 | 108.52 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03492 | 108.52 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03701 | 108.52 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.42 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.42 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0339 | 108.26 | P23:345:MPC:CENTER 3:8810
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0339 | 108.26 | P23:345:MPC:CENTER 3:8820
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.15 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.15 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.15 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.13 | P23:345:MPC:PRAIRIE3:4470
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.13 | P23:345:MPC:PRAIRIE3:4450
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03391 | 108.13 | P23:345:MPC:PRAIRIE3:4440
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03479 | 107.92 | P42:345:NPPD:BKR-HOS-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03319 | 107.81 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.78 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.78 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.78 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.78 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.78 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.78 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 107.78 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.77 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.77 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.77 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 107.77 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 107.68 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 107.64 | P23:345:XEL:8P6 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03362 | 107.58 | P12:230:XEL-MH:AUTO-SINGLE:PEACEGARD5:GLENBOR4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 107.52 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:MAPLER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.42 | P23:345:XEL:8P5 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.37 | P12:345:XEL:ASAK-ECL SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.37 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.35 | P12:345:XEL:ASK-ECL SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.35 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.35 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.35 | P24:345:XEL:8E7 ECL BS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03366 | 107.33 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03366 | 107.33 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03564 | 107.24 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03565 | 107.16 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03565 | 107.16 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03217 | 107.16 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03217 | 107.16 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03217 | 107.16 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 107.15 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 107.15 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03565 | 107.14 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03565 | 107.14 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03373 | 107.13 | P42:345:NPPD:BKR-SW-3308
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03258 | 107.12 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03562 | 107.07 | P23:345:XEL:492 BKR SPK AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03452 | 107.06 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 107.06 | P12:345:XEL:ASAK-ECL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03234 | 107.04 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03373 | 106.98 | P42:345:NPPD:BKR-SW-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03431 | 106.96 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03398 | 106.91 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03376 | 106.86 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04126 | 106.83 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03373 | 106.81 | P21:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03373 | 106.81 | P12:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03372 | 106.81 | P23:345:XEL:8N46 QRY
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04126 | 106.78 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03503 | 106.66 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03779 | 106.62 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03779 | 106.61 | P12:345:UMZ:# 5869 #: IN . PROPER N-1 (LINE) FOR 652529-652829-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03779 | 106.61 | P12:345:UMZW:# 1682 #: WT2 IN SD. WT2-WHT LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.6 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03458 | 106.6 | P12:230:XEL:MNV-GRA-PTH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.59 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 106.57 | P23:345:XEL:8E5 ECL BS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03779 | 106.57 | P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION WO A FAULT (WT2-WT2LNX3 LINE REACTOR)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.54 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03376 | 106.51 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03503 | 106.5 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03405 | 106.44 | P12:230:OTP::HANKSON4:OAKES 4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 106.43 | P12:230:OTP:AUTO-SINGLE:WAHPETN4:FERGSFL4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03404 | 106.42 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.38 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.38 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.38 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.37 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.36 | P55:345:ATC:ARPIN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 106.32 | P11:115:UMZZ:# 2991 #: BH IN SD. LOSS OF BEETHOVEN WIND FARM
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.31 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.31 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03466 | 106.26 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03425 | 106.25 | P12:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03425 | 106.25 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.24 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03404 | 106.17 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.17 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:GRE-HENNING4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03433 | 106.13 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0354 | 106.12 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0354 | 106.12 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03294 | 106.11 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03432 | 106.11 | P12:230:XEL:AUTO-SINGLE:MNVLTAP4:GRE-PANTHER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.1 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03526 | 106.1 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.09 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.09 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.09 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 106.09 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0354 | 106.09 | P23:345:WAPA:SIOUXCY:8692
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.034 | 106.08 | P42:345:NPPD:BKR-GGS-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0338 | 106.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0338 | 106.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 106.06 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 106.06 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 106.04 | P12:230:OTP-GRE::GRE-SILVRLK4B2.SLV-INM
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0343 | 106 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03342 | 105.97 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03342 | 105.97 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03395 | 105.93 | P12:230:OTP:AUTO-SINGLE:WILTON4:WINGER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03451 | 105.91 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03415 | 105.88 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0339 | 105.8 | P23:345:XEL:8N5 MNN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.77 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.77 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03409 | 105.76 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.74 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.74 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.74 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.74 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 105.72 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 105.72 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03402 | 105.7 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03402 | 105.7 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03392 | 105.69 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03392 | 105.69 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.61 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:BARNES4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03416 | 105.61 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.57 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.57 | P23:345:MEC:CBEC 908
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 105.57 | P23:345:ALTW:MITCHLCO:1160
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03708 | 105.56 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.54 | P11:345:UMZB:# 15 #: LO IN ND. LELAND OLDS 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.53 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.53 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.52 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 105.49 | P23:345:MEC:CBEC 905
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.49 | P13:230:MDU:TATANKA GSU & COLLECTOR LOSS:TATANKA::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.49 | P12:230:MDU::TATANKA NORTH:TATANKA SOUTH:1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.43 | P13:230-34:OTP:AUTO-SINGLE:BARNES4:ASH19:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.42 | P13:014-115:GRIS:GSUPGS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.42 | P11:115:GRIS:PGS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03402 | 105.41 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03389 | 105.28 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.25 | P23:345:XEL:8N8 MNN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.25 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.25 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.25 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.25 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.23 | P11:035:UMZB:# 2985 #: LINDAHL WIND IN ND. LINDAHL WIND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03403 | 105.23 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03403 | 105.22 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03403 | 105.22 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.21 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.21 | P11:345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.21 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.21 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.19 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.19 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.19 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.19 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.19 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.18 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.18 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.18 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.17 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.17 | P13:18-345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.17 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.17 | P11:345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.15 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.14 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.13 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.13 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.13 | P11:115:XEL:HBR #6 7 8
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.13 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.11 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.11 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.11 | P13:23-345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.11 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.09 | P11:115:UMZB:# 34 #: PWN IN ND. NDPRARIE WINDS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.08 | P12:115:UMZ:# 5700 #: IN . PROPER N-1 (LINE) FOR 655946-655947-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.08 | P12:116:UMZB:# 2911 #: LND IN ND. LINDAHL - NESET
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.07 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.03 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.03 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.02 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.02 | P11:22:AEPW:NES3-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 105.02 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 105.02 | P11:230:MDU::TATANKA::W::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.99 | P11:22:AEPW:FLINTCR1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.99 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.98 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.98 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.98 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.98 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.98 | P13:161-22:AEPW:FLINTCR5
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.98 | P12:HV:EES::FLINTCR5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.97 | P11:035:UMZW:# 28 #: WWC IN SD. LOSS OF UNIT (WIND).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.97 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.96 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.96 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.96 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.95 | P11:035:UMZB:# 2984 #: BRADY WIND IN ND. BRADY WIND 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.94 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.94 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.94 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.94 | P23:345:XEL:8P1 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.93 | P11:115:XEL:HBR #7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.93 | P11:115:XEL:HBR #6
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 104.93 | P12:115:UMZ:# 5537 #: IN . PROPER N-1 (LINE) FOR 652421-659262-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.93 | P11:15:XEL:AUTO-SINGLE:MEC-CT1:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.93 | P11:014:UMZB:# 41 #: WILT3 IN ND. WILTON 3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P12:115:OTP:AUTO-SINGLE:COURTENAYW7:JAMSTWN7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P11:22:EES-EAI:ARK_NU:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P11:19:XEL:AUTO-SINGLE:MEC-ST:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P23:345:XEL:8S24 WLM AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P12:EHV:EES::8ANO%:1(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.92 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 104.92 | P12:115:UMZB:# 2944 #: CQ IN MT. POPLAR - WILLISTON
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 104.92 | P12:115:UMZ:# 5798 #: IN . PROPER N-1 (LINE) FOR 659112-659262-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.91 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.91 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.91 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.91 | P12:115:XEL:AUTO-SINGLE:WILMART7:MEC-115:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.9 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.9 | P12:EHV:EES::8ANO%:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.9 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.9 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.89 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.89 | P11:115:UMZB:# 2 #: CQ IN ND. CULBERTSON GEN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.89 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.89 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.88 | P11:0:OTP:AUTO-SINGLE:ASH2GEN9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.87 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.87 | P13:230-34:OTP:AUTO-SINGLE:SIBLEY4:ASH39:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.87 | P11:0:OTP:AUTO-SINGLE:ASH3GEN9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.86 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.86 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.86 | P11:18:XEL:AUTO-SINGLE:HBRC72G:8
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.86 | P11:18:XEL:AUTO-SINGLE:HBRC71G:7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.85 | P11:18:XEL:AUTO-SINGLE:COLVILLG:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.85 | P11:18:XEL:AUTO-SINGLE:COLVILL1G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.85 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.85 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.84 | P12:230:OTP:AUTO-SINGLE:BARNES4:SIBLEY4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.84 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.83 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.83 | P11:014:UMZB:# 39 #: WILT1 IN ND. WILTON 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.83 | P11:16:GRE:AUTO-SINGLE:GRE-ER14G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.82 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03487 | 104.82 | P24:345:ITCM:LAKEFLD 885 FUT:MN
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.82 | P23:345-161:XEL:ADAMS_I:681_S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.82 | P23:345-161:XEL:ADAMS_I:680_S
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.82 | P41:345:OKGE:SB_SOER7382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.82 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.82 | P11:001:UMZB:# 26 #: WILT2 IN ND. WILTON 2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P11:230:WERE:JECU1_GEN::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P11:345:WERE:JECU2_GEN::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P23:345:WERE:JEC_345-15::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.81 | P11:115:MDU::HESKETT::3::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P13:115:MDU:HESKETT 3 GSU LOSS:HESKETT::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P11:345:WERE:JECU3_GEN::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.81 | P23:345:WERE:JEC_345-19::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.8 | P13:230:MDU:HETTINGER GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.8 | P13:230:MDU:THUNDER SPIRIT & G752-2 GSUS & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.8 | P13:230:MDU:THUNDER SPIRIT GSU & COLLECTOR LOSS:HETTINGER::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.8 | P23:345:WERE:JEC_345-20::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 104.79 | P23:345:XEL:8P2 KING
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.78 | P41:345:OKGE:SB_SEOL7383
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.78 | P41:345:OKGE:SB_SEOL7382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.77 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.77 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.76 | P23:345:WERE:JEC_345-16::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.75 | P11:115:MDU::LEWIS & CLARK::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.73 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.73 | P11:230:MDU::THUNDER SPIRIT::W::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.72 | P11:230:MDU::G752-2::W::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.72 | P12:115:XEL:DLK-HYL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.7 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P12:EHV:EES::MUSKOGE7!:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P41:345:OKGE:SB_MUGE7384
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG6G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.69 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG5G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.68 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.67 | P11:014:UMZW:# 80 #: OA IN SD. LOSS OF UNIT (5).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.67 | P11:014:UMZW:# 81 #: OA IN SD. LOSS OF UNIT (6).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.67 | P11:014:UMZW:# 82 #: OA IN SD. LOSS OF UNIT (7).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.67 | P11:014:UMZW:# 78 #: OA IN SD. LOSS OF UNIT (3).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.67 | P11:014:UMZW:# 77 #: OA IN SD. LOSS OF UNIT (2).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.67 | P11:014:UMZW:# 79 #: OA IN SD. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.66 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.64 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 104.63 | P13:115-230:NPPD:NUCOR-3
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.63 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB19:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.63 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB29:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.63 | P11:0:OTP:AUTO-SINGLE:J263COURTW:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.63 | P11:0:OTP:AUTO-SINGLE:J262COURTW:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.62 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.62 | P11:014:UMZW:# 46 #: BG IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.57 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.5 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:LUVERNE4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.5 | P12:230:OTP-MPC:B2.PB4-LUV
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.49 | P13:230-34:OTP:AUTO-SINGLE:LUVERNE4:ASH29:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.45 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.43 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.43 | P11:0:XEL:AUTO-SINGLE:J183PROSEW2:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.42 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.42 | P11:0:XEL:AUTO-SINGLE:J183PROSEW1:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03399 | 104.35 | P13:230-345:NPPD:NUCOR-1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.32 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.3 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03421 | 104.3 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.27 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 104.21 | P23:345:SUNC:MO_BRK182
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 104.21 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 104.21 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03657 | 104.21 | P12:230:UMZW:# 686 #: FT IN SD. FT-OA4 LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03657 | 104.21 | P12:230:UMZW:# 685 #: FT IN SD. FT-OA3 LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03415 | 104.2 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03415 | 104.2 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03415 | 104.19 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.19 | P11:18:ITCM:EMERYGT1:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.18 | P11:18:ITCM:EMERYGT2:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03419 | 104.18 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03414 | 104.18 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.18 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.17 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.17 | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.16 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.16 | P23:500:EES-EAI:KEO:B4921
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.15 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.15 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.14 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03434 | 104.14 | P12:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03434 | 104.14 | P21:345:MEC-WAPA:AUTO-SINGLE:RAUN3:SIOUXCY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.12 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03417 | 104.12 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.11 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.11 | P13:34-161:ALTW:AUTO-SINGLE:G735_WF5:CRYSTLKII5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.11 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CRYSTLKII5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03398 | 104.11 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 104.06 | P23:345:MEC:MADISON CO 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 104.06 | P23:500:EES-EAI:KEO:B4941
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.05 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.05 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03418 | 104.04 | P42:345:NPPD:BKR-RW-3302
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.04 | P13:161-69:ITCM:LIME CK5 T1:IA-NW
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 104.03 | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 104.01 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03418 | 103.99 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03418 | 103.99 | P23:345:SUNC:MO_BRK388
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03418 | 103.99 | P23:345:SUNC:MO_BRK188
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.96 | P23:345:MEC:HIGHLAND 906
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03757 | 103.96 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03757 | 103.96 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03757 | 103.96 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03757 | 103.96 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.95 | P23:345:GMO:SIBLEY_R1-3::SIBLEY-OVERTON-KETCHEM-SIBLEYREA
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.94 | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03751 | 103.93 | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.76 | P13:13-115:GRE-OTP:AUTO-SINGLE:GRE-SPRITWDG:SPIRITWD7:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.72 | P11:16:GRE:AUTO-SINGLE:GRE-CGS82G:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03418 | 103.71 | P42:345:NPPD:BKR-AXT-3302
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.7 | P23:345:XEL-SMMPA:8H9 PRI AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.68 | P23:345:XEL:8S98 NRH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.66 | P23:345:XEL-SMMPA:8H8 PRI AS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03408 | 103.58 | P12:115:GRE:VLT-MCH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.58 | P42:345:NPPD:BKR-MOR-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03416 | 103.53 | P23:345:MEC:KOSSUTH 904
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03416 | 103.53 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03416 | 103.53 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.53 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.53 | P21:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03415 | 103.51 | P42:345:NPPD:BKR-AXT-3308
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.48 | P23:345:GRE:PVS 19JB4
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.47 | P23:345:GRE:PVS 19JB1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.45 | P13:230-34:XEL:AUTO-SINGLE:PEACEGARD5:PEACEGARD9:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.45 | P11:0:XEL:AUTO-SINGLE:J290BORDRW:W
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.43 | P23:345:MEC:GDMEC 902
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.43 | P23:345:MEC:GDMEC 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.41 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.41 | P12:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.41 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.41 | P23:345:MEC:BONDURANT 906
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.4 | P42:345:NPPD:BKR-MOR-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.38 | P23:345:MEC:SYCAMORE 902
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.37 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.37 | P23:345:MEC:MONTEZUMA 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.37 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.37 | P23:345:MEC:SYCAMORE 901
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.32 | P23:345:SMP:BYRON 3-GRE-PL VLLY3 BKR8S16
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.32 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03412 | 103.31 | P24:345:SMP:BYRON 3-BUS TIE BKR8S15
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.25 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.24 | P13:115:MDU:HESKETT 2 GSU LOSS:HESKETT::1::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.23 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 103.22 | P23:345:MEC:MONTEZUMA 903
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03388 | 103.22 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.12 | P11:024:DPC:ALMA2:6
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.12 | P11:24:DPC:AUTO-SINGLE:JPM:6
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0341 | 103.09 | P11:115:MDU::HESKETT::2::::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03413 | 103.07 | P23:345:XEL:8S97 NRH
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0342 | 102.83 | P23:345:XEL:8S72 HNA
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03411 | 102.82 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03409 | 102.6 | P12:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03409 | 102.6 | P21:345:XEL-ALTW:AUTO-SINGLE:LKFLDXL3:LAKEFLD3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03409 | 102.6 | P21:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03409 | 102.6 | P12:345:XEL:AUTO-SINGLE:HELENA3:SHEASLK3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03374 | 102.24 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03408 | 102.14 | P21:345:UMZW:# 325 #: GI IN NE. GI-MCCOOL LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03441 | 102.12 | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03441 | 102.12 | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03441 | 102.12 | P12:345:MEC:OBRIEN-LAKEFIELD + REACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03441 | 102.12 | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0344 | 102.01 | P12:345:MEC:OBRIEN-HIGHLAND AND REACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0344 | 102.01 | P21:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0344 | 102.01 | P12:345:MEC:AUTO-SINGLE:OBRIEN3:HIGHLND3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0344 | 102 | P23:345:MEC:HIGHLAND 903
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0344 | 102 | P23:345:MEC:HIGHLAND 902
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03441 | 101.8 | P23:345:MEC:OBRIEN 904
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0345 | 101.28 | P23:345:MEC:OBRIEN 903
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03219 | 100.94 | P13:115-345:NPPD:ANTELOPE:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 130.31 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03589 | 122.85 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03624 | 120.28 | P12:230:UMZB:# 111 #: ST IN SD. WESSINGTION SPRINGS-STORLA-VT HANLON
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 119.55 | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 119.55 | P21:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.74 | P12:500:MH:M602F
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.74 | P21:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.74 | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.42 | P21:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.42 | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03431 | 118.37 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03431 | 118.37 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.23 | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03449 | 118.23 | P21:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0343 | 118.17 | P24:500:MP:FBS:601LX
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03631 | 118.15 | P23:345:XEL:192 BKR SPK AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03632 | 118.15 | P23:345:XEL:196 BKR SPK AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03621 | 118.15 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03621 | 118.15 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03622 | 117.84 | P12:230:UMZW:# 692 #: FT IN SD. FT-LET LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03431 | 117.69 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03431 | 117.69 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0432 | 117.57 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04299 | 117.53 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03715 | 116.95 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03757 | 116.85 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03757 | 116.82 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 116.8 | P21:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03407 | 116.8 | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03404 | 116.49 | P23:345:OTP:BUFFALO3:3615:V2016
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03408 | 116.38 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03379 | 116.29 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03379 | 116.29 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03398 | 116.27 | P23:345:MRES:ALEXMRES3:3385:FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0338 | 116.25 | P23:345:OTP:CENTER 3:3235
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0338 | 116.25 | P23:345:OTP:CENTER 3:3245
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03379 | 116.17 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03379 | 116.17 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03417 | 116.12 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0352 | 115.5 | P23:345:XEL:8X25 NOB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0352 | 115.5 | P23:345:XEL:8X24 NOB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0352 | 115.47 | P21:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0352 | 115.47 | P12:345:XEL-ALTW:AUTO-SINGLE:NOBLES3:LAKEFLD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0352 | 115.45 | P24:161-345:ITCM:LAKEFLD 8160 T1:MN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03446 | 115.29 | P21:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03446 | 115.29 | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.07 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.07 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.07 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.07 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.07 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.07 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.06 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.06 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.06 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.06 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03478 | 115.06 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03618 | 115.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03446 | 114.97 | P23:345:MPC:PRAIRIE3:4440
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03446 | 114.94 | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03446 | 114.94 | P21:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03446 | 114.93 | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03619 | 114.93 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03619 | 114.93 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03619 | 114.9 | P12:345:UMZW:# 851 #: SC2-SR IN IA. SC2-SR 345 KV LINE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03619 | 114.9 | P12:345:UMZ:# 5865 #: IN . PROPER N-1 (LINE) FOR 652564-652864-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03556 | 114.85 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03556 | 114.85 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03363 | 114.8 | P12:115:NPPD:WAPA6:FTRANDL7:ONEILL 7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03616 | 114.79 | P23:345:XEL:492 BKR SPK AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03421 | 114.3 | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03421 | 114.3 | P21:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03289 | 114.26 | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03547 | 114.24 | P42:345:NPPD:BKR-HOS-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03427 | 114.24 | P42:345:NPPD:BKR-GGS-3316
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03593 | 114.23 | P23:345:WAPA:SIOUXCY:8592-8696
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03593 | 114.23 | P23:345:UMZW:# 853 #: SC2 IN IA. SC2 345 KV BREAKER FAILURE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 114.21 | P12:345:ATC:8E2_GD:ASKING3:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03593 | 114.2 | P23:345:WAPA:SIOUXCY:8692
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03467 | 114.19 | P23:345:XEL:8P6 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03317 | 114.17 | P12:230:WAPA:FTRANDALL-SIOUXCY:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03456 | 114.11 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03272 | 114.11 | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03272 | 114.11 | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03272 | 114.11 | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03422 | 114.08 | P42:345:NPPD:BKR-GGS-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03836 | 114.06 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03538 | 114.06 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03836 | 114.06 | P12:345:UMZ:# 5869 #: IN . PROPER N-1 (LINE) FOR 652529-652829-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03836 | 114.06 | P12:345:UMZW:# 1682 #: WT2 IN SD. WT2-WHT LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03512 | 114.03 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03836 | 114.01 | P21:345:UMZW:# 326 #: WT2 IN SD. OPENING OF A LINE SECTION WO A FAULT (WT2-WT2LNX3 LINE REACTOR)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.96 | P23:345:XEL:8P5 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.92 | P12:345:XEL:ASAK-ECL SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.92 | P22:345:XEL:345KV SEC 2 ECL SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.9 | P12:345:XEL:ASK-ECL SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.9 | P24:345:XEL:8E7 ECL BS SPS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.9 | P24:345:XEL:8E7 ECL BS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.89 | P12:345:ATC:8E2:ASKING3:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03427 | 113.81 | P23:345:XEL:8N46 QRY
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03428 | 113.77 | P12:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03428 | 113.77 | P21:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03491 | 113.72 | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.69 | P12:345:XEL:ASAK-ECL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.68 | P21:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.68 | P12:345:XEL:AUTO-SINGLE:ASKING3:EAUCL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04199 | 113.64 | P12:230:UMZW:# 170 #: WT IN SD. WT-HU LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03564 | 113.6 | P12:230:UMZW:# 172 #: WT IN SD. WT-APD LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0345 | 113.58 | P13:115-230:GRE:RMS TR1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.04199 | 113.58 | P12:230:UMZW:# 169 #: WT IN SD. WT-CRP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03517 | 113.58 | P12:230:XEL:MNV-GRA-PTH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.56 | P12:115:OTP-MRES::HOOT LK7:FERGSFL7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 113.45 | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03564 | 113.42 | P12:230:UMZW:# 136 #: GF IN MN. GF-APD LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 113.36 | P12:230:OTP::HANKSON4:OAKES 4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03332 | 113.33 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 113.31 | P11:115:UMZZ:# 2991 #: BH IN SD. LOSS OF BEETHOVEN WIND FARM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03521 | 113.29 | P12:230:UMZW:# 691 #: FT IN SD. FT-WSG LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03462 | 113.22 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.21 | P12:345:ATC-XEL:8E5_GD:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.17 | P23:345:ATC:ARPIN:424-S_GD
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.15 | P12:230:OTP:AUTO-SINGLE:WAHPETN4:FERGSFL4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03485 | 113.13 | P21:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03485 | 113.13 | P12:345:XEL:AUTO-SINGLE:LYONCO3:GRE-CEDARMT3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03463 | 113.1 | P12:230:OTP:AUTO-SINGLE:HANKSON4:FORMAN4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03389 | 113.09 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03389 | 113.09 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03492 | 113.07 | P12:230:UMZW:# 1720 #: GF IN MN. GF-MNVLTAP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.06 | P23:345:XEL:8E5 ECL BS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 113.05 | P12:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 113.05 | P21:345:XEL:AUTO-SINGLE:NROC3:BRIGGSRD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03491 | 113.04 | P12:230:XEL:AUTO-SINGLE:MNVLTAP4:GRE-PANTHER4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 113.03 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:FERGSFL4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03596 | 113.02 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 113.02 | P23:345:MEC:BLACK HAWK 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03438 | 113 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03438 | 113 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 113 | P13:18-115:HAST::EGYCNTR7 XFMR G2:WEC 2 GSU
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 113 | P11:18:HAST:255 MW:EGYCTR2G WEC2:LOSS OF WEC 2 GEN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.95 | P12:230:OTP:AUTO-SINGLE:GRE-SILVRLK4:GRE-HENNING4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.91 | P12:230:OTP-GRE::GRE-SILVRLK4B2.SLV-INM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 112.91 | P21:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 112.91 | P12:345:XEL-ALTE:AUTO-SINGLE:EAUCL3:ARPINB4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 112.91 | P12:345:ATC-XEL:8E5:ARPINB4:EAUCL3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03489 | 112.9 | P12:230:XEL:AUTO-SINGLE:GRE-PANTHER4:HUC-MCLEOD4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 112.89 | P55:345:ATC:ARPIN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 112.89 | P23:345:XEL:ARPIN:ARP_424-S
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0351 | 112.89 | P12:230:WAPA:TWINCH-SIOUXCY:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03458 | 112.79 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 112.76 | P23:345:ATC:NORTHMADISON:6037-S
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03457 | 112.75 | P12:115:UMZ:# 5576 #: IN . PROPER N-1 (LINE) FOR 652479-659153-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03457 | 112.75 | P12:115:UMZW:# 153 #: MS-VE-MR IN SD. VETAL TAP IS A TAP WITH NON-FAULT INTERUPTERS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.75 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 112.74 | P12:345:ATC-XEL:W-13:NMAB3345:BRIGGSRD
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 112.74 | P21:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 112.74 | P12:345:XEL-MGE:AUTO-SINGLE:BRIGGSRD3:NMAB5345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 112.74 | P23:345:ATC:NORTHMADISON:6033-S
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.67 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 112.65 | P23:345:ITCM:HAZLTON3 9985:IA-NE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0345 | 112.65 | P12:230:UMZB:# 2937 #: HWB IN ND. LOSS OF HERBERT WEBER TAP
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0345 | 112.65 | P12:230:UMZ:# 5541 #: IN . PROPER N-1 (LINE) FOR 652426-659128-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03447 | 112.64 | P23:345:XEL:8N5 MNN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03459 | 112.63 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.62 | P11:014:UMZW:# 72 #: GA IN ND. LOSS OF UNIT (5).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.62 | P11:014:UMZW:# 71 #: GA IN ND. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.56 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.56 | P23:345:MEC:CBEC 908
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.56 | P11:014:UMZW:# 69 #: GA IN ND. LOSS OF UNIT (2).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.56 | P11:014:UMZW:# 68 #: GA IN ND. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.56 | P11:014:UMZW:# 70 #: GA IN ND. LOSS OF UNIT (3).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.54 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.53 | P23:345:MEC:CBEC 905
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 112.5 | P13:230:UMZW:# 2144 #: FP IN MT. LOSS OF TRANSFORMER (AT2).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03758 | 112.5 | P12:115:UMZW:# 1843 #: YJ IN SD. YJ-GP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.44 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.43 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 112.43 | P21:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 112.43 | P12:345:ALTW:AUTO-SINGLE:HAZLTON3:MITCHLCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.43 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.4 | P11:138:OKGE:BKRBKR_GSU21
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 112.37 | P12:230:GRE-WAPA:AUTO-SINGLE:GRE-STANTON4:LELANDO4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03459 | 112.34 | P12:230:UMZ:# 5549 #: IN . PROPER N-1 (LINE) FOR 652437-657759-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.3 | P13:014-115:GRIS:GSUPGS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.3 | P11:115:GRIS:PGS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.29 | P13:115-13:OTP:AUTO-SINGLE:HOOTLK7:HOOTLK3G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03582 | 112.28 | P12:115:UMZ:# 5614 #: IN . PROPER N-1 (LINE) FOR 652626-660007-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03582 | 112.28 | P12:115:UMZZ:# 228 #: MEN IN SD. MENNO JUNCTION IS A TAP (UJ-MEN-TP).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.28 | P11:13:OTP:AUTO-SINGLE:HOOTLK3G:3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.23 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.23 | P23:500:EES-EAI:ARK_NU:B5106
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.22 | P42:500:OKGE:SB_FTTH8583
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.22 | P13:115:MKEC:FORTDODGE_GSU::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.22 | P11:115:MKEC:FORTDDODGE_4:143:539670(4)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03432 | 112.17 | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03464 | 112.16 | P23:345:XEL:8M54 SCO
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03464 | 112.16 | P23:345:XEL:8M53 SCO
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03464 | 112.14 | P12:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03464 | 112.14 | P21:345:XEL:AUTO-SINGLE:HELENA3:SCOTTCO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.12 | P23:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.12 | P22:345:OPPD:S3458 NEBCTY2G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.12 | P11:345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.11 | P11:345:MEC-OPPD:NEBRASKA CITY 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.11 | P22:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.11 | P11:345:OPPD:NEBCTY1G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.11 | P23:345:OPPD:S3458 NEBCTY1G:LT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.1 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.1 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.1 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.1 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.1 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 112.09 | P11:345:MEC-OPPD:NEBRASKA CITY 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P11:345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P23:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P13:18-345:OPPD:NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P22:345:OPPD:S3458 NEBCTY1G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P13:23-345:OPPD:NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P23:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.08 | P22:345:OPPD:S3458 NEBCTY2G
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.05 | P11:014:UMZW:# 58 #: FP IN MT. LOSS OF UNIT (4).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.04 | P11:115:UMZB:# 36 #: GGS2 IN SD. GROTON 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03462 | 112.04 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 112.03 | P12:161:XEL-GRE:AUTO-SINGLE:GRNDMDOW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03462 | 112.02 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03462 | 112.02 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.98 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS52G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.98 | P11:16:GRE:AUTO-SINGLE:GRE-PVS52G:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.98 | P12:161:XEL-GRE:AUTO-SINGLE:PLSVLLYW5:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.97 | P11:16:GRE:AUTO-SINGLE:GRE-PVS51G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.97 | P13:16-161:GRE:AUTO-SINGLE:GRE-PVS51G:GRE-PLVLLY5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.97 | P11:0:OTP:AUTO-SINGLE:ASH1GEN9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.96 | P23:345:XEL:8N8 MNN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.93 | P12:116:UMZB:# 2911 #: LND IN ND. LINDAHL - NESET
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.93 | P12:115:UMZ:# 5700 #: IN . PROPER N-1 (LINE) FOR 655946-655947-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.92 | P11:115:UMZB:# 34 #: PWN IN ND. NDPRARIE WINDS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 111.91 | P11:230:MDU::TATANKA::W::::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.9 | P41:345:AEPW:NES CB 3417B NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.9 | P23:345:AEPW:NES CB 3417B NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.9 | P41:345:AEPW:NES CB 3413B NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.9 | P23:345:AEPW:NES CB 3413B NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.9 | P11:22:AEPW:NES3-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.89 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.88 | P13:345-22:AEPW:N.E.S.-7_#1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.88 | P11:22:AEPW:RSS2-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.88 | P11:24:AEPW:RSS1-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.87 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.87 | P13:138-22:AEPW:R.S.S.-4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.87 | P13:138-24:AEPW:R.S.S.-4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.86 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS31G:GRE-LGS32G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.85 | P11:22:AEPW:FLINTCR1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.84 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS35G:GRE-LGS36G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.84 | P13:345-13-13:GRE:AUTO-SINGLE:GRE-LKFDGEN3:GRE-LGS33G:GRE-LGS34G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.83 | P13:161-22:AEPW:FLINTCR5
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.82 | P11:035:UMZW:# 28 #: WWC IN SD. LOSS OF UNIT (WIND).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.81 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.81 | P11:035:UMZB:# 3563 #: IN ND. ND SUNFLOWER WIND
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.8 | P11:115:SUNC:HOLCOMB_1:384:531447(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.8 | P13:115:SUNC:HOLCOMB_GSU::
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.8 | P12:115:XEL:AUTO-SINGLE:ODELLWIND7:WOADHILL7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.8 | P13:345-115:XEL:AUTO-SINGLE:WOADHILL3:WOADHILL7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.79 | P11:22:EES-EAI:ARK_NU:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.79 | P21:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.79 | P12:345:XEL:AUTO-SINGLE:WOADHILL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 111.79 | P23:345:XEL:8S24 WLM AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.79 | P11:15:XEL:AUTO-SINGLE:MEC-CT1:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03466 | 111.78 | P12:115:UMZ:# 5537 #: IN . PROPER N-1 (LINE) FOR 652421-659262-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.78 | P13:500:EES-EAI:ARK_NU:T2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.78 | P21:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.78 | P12:345:XEL:AUTO-SINGLE:WILMART3:MEC-345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.78 | P11:19:XEL:AUTO-SINGLE:MEC-ST:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.78 | P13:19-345:XEL:AUTO-SINGLE:MEC-ST:MEC-345:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.78 | P23:345:XEL:8P1 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.77 | P11:115:UMZB:# 2 #: CQ IN ND. CULBERTSON GEN
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.77 | P11:22:EES-EAI:ARK_NU:1:D395
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.76 | P13:500:EES-EAI:ARK_NU:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03466 | 111.76 | P12:115:UMZ:# 5798 #: IN . PROPER N-1 (LINE) FOR 659112-659262-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03466 | 111.76 | P12:115:UMZB:# 2944 #: CQ IN MT. POPLAR - WILLISTON
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.76 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.75 | P12:115:XEL:AUTO-SINGLE:WILMART7:MEC-115:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.75 | P13:15-115:XEL:AUTO-SINGLE:MEC-CT1:MEC-115:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.75 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.75 | P11:014:UMZB:# 41 #: WILT3 IN ND. WILTON 3
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.75 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.75 | P11:0:OTP:AUTO-SINGLE:ASH2GEN9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.74 | P23:161-345:KCPL:IATAN_R1-11::IATANU1-IATANT11
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.74 | P11:014:UMZB:# 2986 #: PIONEER RECIP A IN ND. PIONEER RECIP PACK A
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.74 | P11:014:UMZB:# 2987 #: PIONEER RECIP B IN ND. PIONEER RECIP PACK B
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.74 | P11:115:XEL:HBR #6
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.74 | P11:115:XEL:HBR #7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.74 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.72 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.72 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.72 | P12:230:OTP:AUTO-SINGLE:BARNES4:SIBLEY4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.72 | P11:0:OTP:AUTO-SINGLE:ASH3GEN9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.72 | P13:230-34:OTP:AUTO-SINGLE:SIBLEY4:ASH39:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.71 | P23:345:XEL:8P2 KING
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.71 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.7 | P11:138:OKGE:BKRBKR_GSU03
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.7 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.7 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P13:138-24:AEPW:TURK 4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:24:AEPW:TURKCOAL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:18:XEL:AUTO-SINGLE:COLVILL1G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:18:XEL:AUTO-SINGLE:COLVILLG:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P13:18-115:XEL:AUTO-SINGLE:COLVILLG:CANONFLSG7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P13:18-115:XEL:AUTO-SINGLE:COLVILL1G:CANONFLSG7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:035:UMZB:# 2983 #: BRADY WIND IN ND. BRADY WIND 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:001:UMZB:# 26 #: WILT2 IN ND. WILTON 2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:014:UMZB:# 39 #: WILT1 IN ND. WILTON 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P11:16:GRE:AUTO-SINGLE:GRE-ER14G:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.68 | P13:16-230:GRE:AUTO-SINGLE:GRE-ER14G:GRE-ELKRIV4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.67 | P11:18:XEL:AUTO-SINGLE:HBRC71G:7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.67 | P11:18:XEL:AUTO-SINGLE:HBRC72G:8
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.67 | P41:345:OKGE:SB_SOER7382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.67 | P11:345:OKGE:BKRBKR_GSU04
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.67 | P13:18-115:XEL:AUTO-SINGLE:HBRC72G:HIBRDGE7:8
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.67 | P13:18-115:XEL:AUTO-SINGLE:HBRC71G:HIBRDGE7:7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.66 | P11:345:OKGE:BKRBKR_GSU27
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.66 | P11:345:OKGE:BKRBKR_GSU26
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 111.65 | P12:115:UMZ:# 5567 #: IN . PROPER N-1 (LINE) FOR 655490-652525-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 111.65 | P12:115:UMZW:# 509 #: TY IN SD. TY-YJ LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.65 | P41:345:OKGE:SB_REUD7381
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.65 | P41:345:OKGE:SB_REUD7383
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.64 | P11:345:OKGE:BKRBKR_GSU25
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.64 | P11:345:OKGE:BKRBKR_GSU24
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.63 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.63 | P41:345:OKGE:SB_SEOL7383
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.61 | P41:345:OKGE:SB_SEOL7382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.6 | P11:345:OKGE:BKRBKR_GSU07
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.6 | P11:345:OKGE:BKRBKR_GSU08
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 111.57 | P12:115:XEL:DLK-HYL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 111.57 | P12:115:XEL:SCO-DLK-HYL-BLL
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.53 | P12:115:XEL:AUTO-SINGLE:NSSJCT7:NSSTAP7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.52 | P12:115:XEL:AUTO-SINGLE:REDROCK7:NSSJCT7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.52 | P23:345:KCPL-WERE:LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.51 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO28:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.51 | P13:115-34:XEL:AUTO-SINGLE:NOBLES7:NOBLESCO18:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.5 | P11:345:OKGE:BKRBKR_GSU06
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.5 | P41:345:OKGE:SB_MUGE7384
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.5 | P11:345:OKGE:BKRBKR_GSU05
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.5 | P11:345:OKGE:BKRBKR_GSU22
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.46 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.45 | P11:014:UMZW:# 46 #: BG IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 111.4 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.39 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB19:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.39 | P13:115-34:OTP:AUTO-SINGLE:COURTENAYW7:COURTB29:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.32 | P12:230:OTP-MPC:B2.PB4-LUV
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.32 | P12:230:OTP:AUTO-SINGLE:PILSBRY4:LUVERNE4:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.31 | P13:230-34:OTP:AUTO-SINGLE:LUVERNE4:ASH29:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03459 | 111.31 | P13:230-345:NPPD:NUCOR-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.29 | P11:035:UMZB:# 3564 #: CBW IN SD. CAMBELL COUNTY WIND 1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.21 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB19:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.21 | P13:115-34:XEL:AUTO-SINGLE:PROSEWIND7:PROSEB29:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.14 | P11:069:UMZB:# 12 #: HY IN SD. HYDE
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03459 | 111.09 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 111.04 | P11:34:ALTW:AUTO-SINGLE:G735_WF5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03726 | 111.04 | P12:230:UMZW:# 684 #: FT IN SD. FT-OA2 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03736 | 111.01 | P12:230:UMZW:# 686 #: FT IN SD. FT-OA4 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03736 | 111.01 | P12:230:UMZW:# 685 #: FT IN SD. FT-OA3 LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.99 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.96 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.94 | P23:345:MEC:MADISON CO 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.94 | P13:115-34:XEL:AUTO-SINGLE:YANKEE7:YANKEEB2:2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.94 | P12:115:OTP-MPC::TRFALLS7:WINGER 7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.93 | P11:18:ITCM:EMERYGT1:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.91 | P11:18:ITCM:EMERYGT2:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.89 | P12:161:ALTW:AUTO-SINGLE:FREEBORN5:G870_TAP5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.88 | P23:345:XEL:8S22 WLM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.87 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.87 | P12:115:XEL:AUTO-SINGLE:SPLTRK7:PROSECAP7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.87 | P12:115:XEL:AUTO-SINGLE:PROSEWIND7:PROSECAP7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.86 | P13:34-161:ALTW:AUTO-SINGLE:G735_WF5:CRYSTLKII5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.85 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CRYSTLKII5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.84 | P21:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.84 | P12:345:XEL:AUTO-SINGLE:WILMART3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.84 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.84 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:FIELD_N3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.84 | P12:115:OTP::DONALDS7:TRFALLS7
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03487 | 110.82 | P21:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03487 | 110.82 | P12:345:ALTW:AUTO-SINGLE:HUNTLEY3:LEDYARD3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.82 | P23:345:MEC:HIGHLAND 906
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.81 | P21:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.81 | P12:345:XEL:AUTO-SINGLE:FIELD_S3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.79 | P13:161-69:ITCM:LIME CK5 T1:IA-NW
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.79 | P12:161:ALTW:AUTO-SINGLE:LIMECKL15:CLKREACT5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.78 | P12:161:ALTW:AUTO-SINGLE:CRYSTLK5:CLKREACT5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03473 | 110.76 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03487 | 110.75 | P42:345:ITCM:HUNTLEY3-LAKEFLD3 3651-3654:IA-MVP
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03499 | 110.74 | P12:230:UMZB:# 109 #: SB IN SD. SULLY BUTTES-WHITLOCK-GLENHAM
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03499 | 110.74 | P12:230:UMZ:# 5605 #: IN . PROPER N-1 (LINE) FOR 655765-655510-1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03832 | 110.73 | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.73 | P23:345:MEC:GDMEC 902
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.72 | P23:345:MEC:GDMEC 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03499 | 110.71 | P12:230:UMZ:# 5867 #: IN . PROPER N-1 (LINE) FOR 655510-655487-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.71 | P21:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03468 | 110.71 | P12:345:XEL:AUTO-SINGLE:LKFLDXL3:CRANDAL3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.7 | P23:345:MEC:BONDURANT 906
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03417 | 110.68 | P12:115:NPPD:1090:AINSWND7:THEDFRD7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.66 | P23:345:MEC:SYCAMORE 902
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.66 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.66 | P23:345:MEC:MONTEZUMA 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.66 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.66 | P23:345:MEC:SYCAMORE 901
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03437 | 110.65 | P13:115-345:NPPD:THEDFRD3:T2
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03838 | 110.63 | P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03486 | 110.61 | P42:345:ITCM:LEDYARD3-HUNTLEY3 5074-5075:IA-MVP
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.59 | P13:13-115:GRE-OTP:AUTO-SINGLE:GRE-SPRITWDG:SPIRITWD7:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.56 | P23:345:XEL-SMMPA:8H9 PRI AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.54 | P23:345:XEL:8S98 NRH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.53 | P23:345:MEC:MONTEZUMA 903
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.0347 | 110.51 | P23:345:XEL-SMMPA:8H8 PRI AS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03455 | 110.44 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.39 | P12:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.39 | P21:345:XEL:AUTO-SINGLE:NROC3:BYRON3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.37 | P23:345:GRE:PVS 19JB4
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.36 | P23:345:GRE:PVS 19JB1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 110.36 | P23:345:SUNC:HLC_BRK282
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.33 | P21:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.33 | P12:345:XEL:AUTO-SINGLE:BYRON3:GRE-PLVLLY3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03838 | 110.29 | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03838 | 110.29 | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03838 | 110.27 | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03838 | 110.27 | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.26 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.18 | P24:345:SMP:BYRON 3-BUS TIE BKR8S15
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.18 | P23:345:SMP:NROC 3-BYRON 3-BKR8S14
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.18 | P23:345:SMP:BYRON 3-GRE-PL VLLY3 BKR8S16
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.18 | P23:345:SUNC:SB_BRK582
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.17 | P23:345:SUNC:MO_BRK382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.17 | P23:345:SUNC:MO_BRK182
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.17 | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.16 | P23:345:SUNC:SB_BRK488
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.15 | P23:345:SUNC:SB_BRK482
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03473 | 110.15 | P42:345:NPPD:BKR-SW-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 110.13 | P23:345:SUNC:HLC_BRK382
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03467 | 110.12 | P12:115:GRE:VLT-MCH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03471 | 110.11 | P42:345:NPPD:BKR-MOR-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03479 | 110.09 | P23:345:MEC:KOSSUTH 904
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03479 | 110.09 | P12:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03479 | 110.09 | P21:345:ALTW-MEC:AUTO-SINGLE:LEDYARD3:KOSSUTH3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03476 | 110.08 | P42:345:NPPD:BKR-GGS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03473 | 110.04 | P42:345:NPPD:BKR-MOR-3306
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03474 | 110.03 | P42:345:NPPD:BKR-SW-3304
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03472 | 110.03 | P23:345:XEL:8S97 NRH
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 110.01 | P13:230-34:XEL:AUTO-SINGLE:PEACEGARD5:PEACEGARD9:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 109.9 | P11:014:UMZW:# 83 #: OA IN SD. LOSS OF UNIT (1).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03473 | 109.88 | P23:345:SUNC:HLC_BRK188
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 109.84 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03477 | 109.69 | P42:345:NPPD:BKR-AXT-3302
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03475 | 109.65 | P42:345:NPPD:BKR-AXT-3308
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03497 | 109.62 | P44:345:ITCM-MEC:LAKEFLD 873 50MVAR:MN-SS
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03497 | 109.62 | P21:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03497 | 109.62 | P12:345:ALTW-MEC:AUTO-SINGLE:LAKEFLD3:OBRIEN3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03443 | 109.52 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 108.97 | P12:115:NPPD:TSGT3:LAMAR 7:GRANTNB7:BTB
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03469 | 108.97 | P12:115:TSGT-BEPC_659:::GRANTNB_-TS7-LAMAR___-TS7-1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03716 | 106.13 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 720 | 0.03838 | 101.14 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 |  | 409 | 0.03227 | 101.66 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | 652550 GRANITF4 230 652582 APPLEDORN 4 230 1 |  | 409 | 0.0322 | 103.96 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z |  | 341 | 0.0301 | 107.02 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997086 SDQ KV2A 230 1 |  | 496 | 0.09153 | 103.31 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997086 SDQ KV2A 230 1 |  | 496 | 0.08939 | 102.38 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997086 SDQ KV2A 230 1 |  | 496 | 0.2414 | 103.31 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997086 SDQ KV2A 230 1 |  | 496 | 0.23581 | 102.38 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997095 SDQ KV2A 230 1 |  | 496 | 0.09062 | 102.38 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997095 SDQ KV2A 230 1 |  | 496 | 0.08861 | 101.68 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997095 SDQ KV2A 230 1 |  | 496 | 0.23821 | 102.38 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659133 SIDNEY__-MB3 345 997095 SDQ KV2A 230 1 |  | 496 | 0.23302 | 101.68 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.09062 | 104.53 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.08861 | 103.8 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.23821 | 104.53 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.23302 | 103.8 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.09153 | 105.53 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.08939 | 104.54 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.2414 | 105.53 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 |  | 478 | 0.23581 | 104.54 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997086 SDQ KV2A 230 1 |  | 496 | 0.09153 | 103.72 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997086 SDQ KV2A 230 1 |  | 496 | 0.08939 | 102.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997086 SDQ KV2A 230 1 |  | 496 | 0.2414 | 103.72 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997086 SDQ KV2A 230 1 |  | 496 | 0.23581 | 102.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997095 SDQ KV2A 230 1 |  | 496 | 0.09062 | 102.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997095 SDQ KV2A 230 1 |  | 496 | 0.08861 | 102.03 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997095 SDQ KV2A 230 1 |  | 496 | 0.23821 | 102.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659210 SIDNEY__-MB4 230 997095 SDQ KV2A 230 1 |  | 496 | 0.23302 | 102.03 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 132.79 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03111 | 132.79 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03558 | 111.57 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03558 | 111.57 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03797 | 111.57 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03797 | 111.57 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03057 | 102.03 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03057 | 102.03 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03296 | 102.03 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03296 | 102.03 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03073 | 119.78 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03073 | 119.78 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03312 | 119.78 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03312 | 119.78 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03785 | 132.56 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03785 | 132.56 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.04024 | 132.56 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.04024 | 132.56 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03152 | 114.04 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.03152 | 114.04 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0339 | 114.04 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 120 | 0.0339 | 114.04 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03111 | 121.06 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03111 | 121.06 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03558 | 101.71 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03558 | 101.71 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03797 | 101.71 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03797 | 101.71 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03073 | 109.26 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03073 | 109.26 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03312 | 109.26 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03312 | 109.26 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03785 | 120.85 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03785 | 120.85 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.04024 | 120.85 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.04024 | 120.85 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03152 | 104.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.03152 | 104.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.0339 | 104.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 659300 STANTN.T-BE7 115 661008 BEULAH 7 115 1 |  | 132 | 0.0339 | 104.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 01ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 01ALL | 2 | N/A | N/A | '' | None |  |  |  |  | None
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.16595 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23676 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23652 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.23463 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.2344 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23732 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23708 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.22678 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.22655 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23902 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23878 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23705 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23681 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.24122 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.24098 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24034 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.2401 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.23824 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.23801 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24093 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24069 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.23039 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.23016 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24263 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24239 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24066 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24042 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24483 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24459 |  | P42:345:OKGE:SB_BAER7314
Thermal | 02ALL | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1 | 389.2 |  | 0.04085 | 104.11 | System Intact
Thermal | 02ALL | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1 | 389.2 |  | 0.04012 | 104.11 | System Intact
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.05339 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.07696 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.07751 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.19822 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.23117 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.75311 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.75311 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.75311 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.07751 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.19822 |  | P23:345:SUNC:HLC_BRK188
Thermal | 03ALL | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | 523853 FINNEY 7 345 588754 G17-032-TAP 345 1 | 380 |  | 1 | 110.65 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-099 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.06019 | 110.14 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-021 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.06019 | 110.14 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 319 |  | 0.03559 | 110.14 | System Intact
Non-Converge | 04ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 04ALL | 2 | N/A | N/A | '' | None |  |  |  |  | None
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.70579 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.70579 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.70579 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.70579 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.70579 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.22876 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.22876 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.08358 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.08358 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.08358 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.08358 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71846 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71846 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71846 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71846 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71846 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08389 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08389 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08389 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08389 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.24126 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.24126 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71623 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71623 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71623 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71623 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.71623 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.23807 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.23807 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08464 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08464 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08464 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.08464 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 06ALL | 2 | N/A | N/A | '' | None |  |  |  |  | None
Non-Converge | 07ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.43386 | 113.33 | P12:345:OKGE-AEPW:BKRBKR371
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 318.7 | 0.36116 | 104.29 | P12:345:OKGE-AEPW:BKRBKR371
Thermal | 07ALL | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.44051 | 101.57 | P12:345:OKGE-AEPW:BKRBKR371
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.43571 | 102.14 | P12:345:OKGE-AEPW:BKRBKR371
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.43386 | 126.83 | P12:345:OKGE-AEPW:BKRBKR371
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.4359 | 114.85 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.4359 | 114.86 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.21482 | 120.18 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.21482 | 102.24 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.21482 | 120.24 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 318.7 | 0.36292 | 105.93 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 318.7 | 0.36292 | 105.94 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.43976 | 100.66 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.43976 | 100.67 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22656 | 101.69 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22656 | 101.8 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.44243 | 103.11 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.44243 | 103.13 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.43772 | 103.98 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.43772 | 103.99 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21721 | 101.61 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21721 | 101.74 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.4359 | 128.53 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.4359 | 128.54 | P42:345:OKGE:SB_GRNT7381
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21482 | 134.48 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21482 | 114.41 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21482 | 134.56 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.30202 | 117.67 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.30202 | 117.6 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.30534 | 113.31 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.30534 | 113.26 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 279 | 0.30276 | 101.94 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 279 | 0.30276 | 101.91 | P42:345:OKGE:SB_GRNT7313
Thermal | 07ALL | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.30349 | 100.49 | P42:345:OKGE:SB_GRNT7313
Non-Converge | 08ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 08ALL | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | 505480 BEAVER 5 161 506932 EUREKA 5 161 1 | 247 |  | 0.03025 | 100.7 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1036 |  | 0.04745 | 107.38 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1036 |  | 0.04907 | 104.68 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1036 |  | 0.05 | 104.23 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1036 |  | 0.0389 | 107.38 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1036 |  | 0.04051 | 104.68 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1036 |  | 0.04146 | 104.23 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69652 | 103.61 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69647 | 102.77 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6919 | 100.42 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72311 | 103.96 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72281 | 103.68 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70721 | 101.74 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71928 | 101.5 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69453 | 101.58 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69449 | 100.78 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72311 | 103.96 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72281 | 103.68 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70721 | 101.74 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71928 | 101.5 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74308 | 105.81 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74375 | 105.76 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74391 | 102.4 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74144 | 101.11 | P12:345:OKGE:BKRBKR357_1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72784 | 99.67 | P12:345:WERE:EMPR-SWIS_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72802 | 100.18 | P12:345:WERE:HOYT-JEC_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72762 | 99.87 | P12:345:WERE:HOYT-JEC_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69453 | 101.58 | P12:345:WERE:N345-PSO_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69449 | 100.78 | P12:345:WERE:N345-PSO_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73022 | 100.47 | P12:345:WERE:RENO-WICH_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7301 | 99.9 | P12:345:WERE:RENO-WICH_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72667 | 99.56 | P12:345:WERE:SWIS-WGAR_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72499 | 123.22 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71435 | 121.6 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.731 | 121.08 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73085 | 119.61 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73116 | 110.82 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73148 | 107.91 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73273 | 105.54 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72499 | 119.56 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71435 | 119.07 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.731 | 116.82 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73085 | 115.45 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73116 | 106.66 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73148 | 103.9 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73273 | 101.48 | P12:345:WERE:WAVS-WOLF_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69293 | 102.97 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6929 | 102.15 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68814 | 99.79 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69293 | 102.97 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6929 | 102.16 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68814 | 99.79 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69293 | 102.78 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6929 | 101.91 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68814 | 99.77 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69652 | 103.61 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69647 | 102.77 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6919 | 100.42 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72003 | 105.74 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71976 | 105.54 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70391 | 103.69 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71594 | 103.06 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72212 | 107.96 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72182 | 107.77 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70453 | 105.67 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71797 | 105.45 | P23:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72311 | 103.96 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72281 | 103.68 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70721 | 101.74 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71928 | 101.5 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72499 | 123.2 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71435 | 121.59 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.731 | 121.04 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73085 | 119.58 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73116 | 110.8 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73148 | 107.92 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73273 | 105.51 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72092 | 122.21 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71049 | 120.56 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72742 | 119.19 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72722 | 117.68 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72737 | 108.29 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72766 | 105.42 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72892 | 102.77 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72663 | 99.63 | P23:345:KCPL-WERE:WGARDNER_R12-13::WGARD-STILWELL-SWISSVALE
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72784 | 99.68 | P23:345:WERE:EMPR_345-210::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72803 | 100.48 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72762 | 100.14 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72801 | 100.25 | P23:345:WERE:JEC_345-17::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72762 | 99.92 | P23:345:WERE:JEC_345-17::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69453 | 101.58 | P23:345:WERE:N345_345-20::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69449 | 100.78 | P23:345:WERE:N345_345-20::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73022 | 100.47 | P23:345:WERE:RENO_345-150::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73011 | 99.88 | P23:345:WERE:RENO_345-150::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73022 | 100.47 | P23:345:WERE:RENO_345-160::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73011 | 99.87 | P23:345:WERE:RENO_345-160::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.728 | 99.51 | P23:345:WERE:STRA_345-100::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72784 | 99.67 | P23:345:WERE:SWIS_345-1::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72771 | 99.81 | P23:345:WERE:SWIS_345-2::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.7267 | 99.72 | P23:345:WERE:SWIS_345-5::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72499 | 120.53 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71435 | 119.54 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.731 | 117.92 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73085 | 116.56 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73116 | 107.7 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73148 | 104.95 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73273 | 102.47 | P23:345:WERE:WAVS_BKRS::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74436 | 100.04 | P23:345:WERE:WICH_345-50::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74388 | 99.56 | P23:345:WERE:WICH_345-50::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72412 | 123.12 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71325 | 121.98 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73021 | 120 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73006 | 118.59 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73039 | 110.29 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73073 | 107.38 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.73203 | 104.82 | P23:345:WERE:WOLF_345-120::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72693 | 100.4 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 99.53 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69293 | 102.97 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6929 | 102.15 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68814 | 99.79 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69293 | 102.97 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6929 | 102.16 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68814 | 99.79 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69293 | 102.78 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6929 | 101.91 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.68814 | 99.77 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69652 | 103.61 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.69647 | 102.77 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.6919 | 100.42 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72003 | 105.74 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71976 | 105.54 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70391 | 103.69 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71594 | 103.06 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72311 | 103.96 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72281 | 103.68 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70721 | 101.74 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71928 | 101.5 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74375 | 101.41 | P42:345:OKGE:SB_RARD7313
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74308 | 101.38 | P42:345:OKGE:SB_RARD7313
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74308 | 105.81 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74375 | 105.77 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74391 | 102.4 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74144 | 101.11 | P42:345:OKGE:SB_RARD7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74308 | 105.81 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74375 | 105.76 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74391 | 102.4 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.74144 | 101.11 | P42:345:OKGE:SB_SOER7383
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72212 | 107.96 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72182 | 107.77 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.70453 | 105.67 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.71797 | 105.45 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72693 | 100.4 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 |  | 956 | 0.72665 | 99.53 | P46:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 20G | GEN-2017-068 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.08706 | 109.9 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-068 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.07573 | 101.61 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-086 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.07271 | 109.9 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-086 | 'FROM -> TO' | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 1141 |  | 0.06219 | 101.61 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05407 | 121.31 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.0544 | 106.62 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05456 | 105.91 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05498 | 103.81 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.05184 | 99.76 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07407 | 121.31 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.0744 | 106.62 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07456 | 105.91 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07498 | 103.81 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-022 | 'FROM -> TO' | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 205 |  | 0.07184 | 99.76 | System Intact
Non-Converge | 09ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 09ALL | 2 | N/A | N/A | " | None |  |  |  |  | None
Non-Converge | 10ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 10ALL | 2 | N/A | N/A | '' | None |  |  |  |  | None
Non-Converge | 12ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 12ALL | 2 | N/A | N/A | '' | None |  |  |  |  | None
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06237 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06237 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06237 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06237 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06237 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06171 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06171 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06171 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06171 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06171 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06049 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06049 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06049 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06049 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06049 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07386 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07386 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07386 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07386 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.07386 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06127 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06127 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06127 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06127 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06127 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06427 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06427 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06427 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06427 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06427 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06082 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06082 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06082 |  | P22:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06082 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06082 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 14ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.31027 | 102.61 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30767 | 99.5 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.30767 | 99.5 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | 510918 VALIANT4 138 520948 HUGO PP4 138 1 |  | 287 | 0.31021 | 100.21 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Non-Converge | 15ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 15ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 15NR | 2 | 20G | GEN-2017-094 | 'FROM -> TO' | 652552 SIOUXCY2 230 652565 SIOUXCY4 230 Z |  | 341 | 0.0333 | 126.01 | P23:345:MEC:RAUN 0270
Non-Converge | 16ALL | 0 | N/A | N/A | '' | None |  |  |  |  | None
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 400 |  | 0.09675 | 108.83 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 400 |  | 0.12528 | 108.83 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 400 |  | 0.09626 | 112.41 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 400 |  | 0.1248 | 112.41 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 400 |  | 0.09423 | 109.59 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 400 |  | 0.12169 | 109.59 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.8888 | 140.65 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88883 | 139.83 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88892 | 139.69 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24L | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88903 | 139.31 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.889 | 138.14 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88879 | 131.97 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88881 | 130.62 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.8888 | 140.65 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88883 | 139.83 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88892 | 139.69 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 24L | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.88903 | 139.31 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 506 | 0.889 | 138.14 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88879 | 131.97 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z |  | 526 | 0.88881 | 130.62 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 400 |  | 0.09675 | 113.27 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 400 |  | 0.12528 | 113.27 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 400 |  | 0.09626 | 117.6 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 400 |  | 0.1248 | 117.6 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 400 |  | 0.09423 | 114.17 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 400 |  | 0.12169 | 114.17 | System Intact
Thermal | 16ALL | 2 | 20G | GEN-2017-010 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 400 |  | 0.08907 | 100.16 | System Intact
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 400 |  | 0.11653 | 100.16 | System Intact
Non-Converge | 17ALL | 0 | N/A | N/A |  | None |  |  |  |  | None
Thermal | 17ALL | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.76 | System Intact
Thermal | 17ALL | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.64 | System Intact
Thermal | 17ALL | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.77 | System Intact
Thermal | 17ALL | 2 | 24L | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.2 | System Intact
Thermal | 17ALL | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.57 | System Intact
Thermal | 17ALL | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.62 | System Intact
Thermal | 17ALL | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 588590 GEN-2017-014 230 659188 PHILIP_T-BE4 230 1 | 160 |  | 1 | 184.45 | System Intact
Thermal | 17ALL | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23277 | 110.98 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23177 | 119.22 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17ALL | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23629 | 113.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17ALL | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23616 | 115.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17ALL | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23299 | 110.63 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17ALL | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.23652 | 113.78 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 02ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 02NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 03ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 03NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 04ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 04NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 06ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 06NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 07ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 08ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 08NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 09ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 09NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 10ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 12ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 13ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 14ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 14NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 15ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 15NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 16ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 17ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 17NR | 3 | N/A | N/A | None | [7 empty] | None

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS1701TC01ALL-24WP0.SAV |  | DIS1701TC01ALL-29SP0.SAV |  | DIS1701TC02ALL-24WP0.SAV |  | DIS1701TC02ALL-29SP0.SAV |  | DIS1701TC03ALL-24WP0.SAV |  | DIS1701TC03ALL-29SP0.SAV |  | DIS1701TC04ALL-24WP0.SAV |  | DIS1701TC04ALL-29SP0.SAV |  | DIS1701TC06ALL-24WP0.SAV |  | DIS1701TC06ALL-29SP0.SAV |  | DIS1701TC07ALL-24WP0.SAV |  | DIS1701TC07ALL-29SP0.SAV |  | DIS1701TC08ALL-24WP0.SAV |  | DIS1701TC08ALL-29SP0.SAV |  | DIS1701TC09ALL-24WP0.SAV |  | DIS1701TC09ALL-29SP0.SAV |  | DIS1701TC10ALL-24WP0.SAV |  | DIS1701TC10ALL-29SP0.SAV |  | DIS1701TC12ALL-24WP0.SAV |  | DIS1701TC12ALL-29SP0.SAV |  | DIS1701TC13ALL-24WP0.SAV |  | DIS1701TC13ALL-29SP0.SAV |  | DIS1701TC14ALL-24WP0.SAV |  | DIS1701TC14ALL-29SP0.SAV |  | DIS1701TC15ALL-24WP0.SAV |  | DIS1701TC15ALL-29SP0.SAV |  | DIS1701TC16ALL-24WP0.SAV |  | DIS1701TC16ALL-29SP0.SAV |  | DIS1701TC17ALL-24WP0.SAV |  | DIS1701TC17ALL-29SP0.SAV
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
Short Circuit Ratio calculation not applicable in DISIS Phase 2.