## DIS1701-P2_Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name | Detail
01ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
01ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 55 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 70 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Grapevine 345kV New Substation (DISIS-2017-001) | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK188 | [7 empty] | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Build approximately 65 miles of new 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 55 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 70 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Grapevine 345kV New Substation (DISIS-2017-001) | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 24L | P23:345:SUNC:HLC_BRK282 | [7 empty] | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Build approximately 65 miles of new 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (ITCGP) | Build approximately 55 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Clark County 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 70 miles of new 345kV line from Beaver County to Clark County
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (OKGE) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Beaver County to Grapeveine 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 45 miles of new 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Grapevine 345kV New Substation (DISIS-2017-001) | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (AEPW) | Build approximately 35 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Grapevine to Chisholm 345kV New Line (DISIS-2017-001) (SWPS) | Build approximately 40 miles of new 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24WP, 29SP | P42:345:OKGE:SB_BAER7314 | [7 empty] | Potter County to Grapevine 345kV New Line (DISIS-2017-001) | Build approximately 65 miles of new 345kV line from Potter County to Grapevine
02ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
03ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
03ALL | ERIS | Thermal | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 26G | System Intact | 160 |  |  | 100.26 |  |  |  | Degrassee 138kV Terminal Upgrades (DISIS-2017-001) (OKGE) | Upgrade terminal equipment at Degrasse 138kV to achieve a minimum Spring/Emergency rating of 175 MVA
03ALL | ERIS | Thermal | 515853 DGRASSE4 138 520436 ROSEVLY4 138 1 | 26G | System Intact | 160 |  |  | 100.26 |  |  |  | Rose Valley to Degrasse 138kV Rebuild (DISIS-2017-001) (WFEC) | Rebuiuld the existing Rose Valley to Degrasse 138kV 3.2 mile line to achieve a minimum Spring/Emergency rating of 175 MVA
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 588754 G17-032-TAP 345 1 | 29S | System Intact | 380 |  |  | 111.75 |  |  |  | Finney to G17-032 Tap 345kV Rebuild (DISIS-2017-001) | Rebuild the existing Finney to G17-032 Tap 345kV 78.75 mile line to achieve a minimum Summer/Emergency rating of 425 MVA
03ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 24L | System Intact | 319 |  |  | 104.17 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA
03ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 24L | System Intact | 319 |  |  | 104.17 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (WERE) | Rebuild the existing Smokey Hills to Summit 230kV 22.5 mile line to achieve a minimum Light/Emergency rating of 375 MVA
04ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
04ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw 765/345kV New Substation (DISIS-2017-001) | Build a new Crawfish Draw 765/345kV Substation tapping the Tuco to Border 345kV Ckt 1 and Tuco to OKU 345kV Ckt 1
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw 765/345kV New Transformer (DISIS-2017-001) | Install a new 765/345kV Transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (OKGE) | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to Border 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Tap Tuco to Border 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (AEPW) | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw Tap to Tuco to OKU 345kV Ckt 1 (DISIS-2017-001) (SWPS) | Tap Tuco to OKU 345kV Ckt 1 and reroute through Crawfish Draw 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (OKGE) | Build approximately 80 miles of new double circuit 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crawfish Draw to Seminole 765kV New Line Double Circuit (DISIS-2017-001) (SWPS) | Build approximately 265 miles of new double circuit 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crossroads 765/345kV New Transformer (DISIS-2017-001) | Expand Crossroads 765kV Substation and install a new 765/345 transformer
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Crossroads to Crawfish Draw 765kV New Line (DISIS-2017-001) | Build approximately 85 miles of new 765kV line from Crossroads to Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | [7 empty] | Seminole 765/345 New Transformer (DISIS-2017-001) | Expand Seminole 765kV Substation and install a new 765/345kV transformer
06ALL | ERIS | Thermal | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 20G, 20SP, 24L, 24SP, 29SP | P12:115:SPS:W59.1.LOPEZ.CMPBLL |  | 128.1 | 87.64 | 114.39 |  |  |  | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA
06ALL | ERIS | Thermal | 524502 NORTON 3 115 524768 PLSNT_HILL 3 115 1 | 20G, 20SP, 24L | System Intact | 128.1 |  | 84.51 | 111.11 |  |  |  | Norton to Pleasant Hills 115kV Rebuild (DISIS-2017-001) | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum Light/Emergency rating of 150 MVA
06ALL | ERIS | Thermal | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 20G | System Intact | 80 |  | 25.91 | 114.43 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 96 MVA, no mitigation is required
06ALL | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 478 | 36.66 | 122.08 |  |  |  | Tolk to Tuco 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum Spring/Emergency rating of 600 MVA
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998079 ABBXNL844501 230 1 | 19WP, 24L, 24SP, 24WP, 29SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 71.21 | 204.34 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 20SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 61.87 | 175.5 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998083 ABBXNL844501 230 1 | 20SP | System Intact | 478 |  | 67.48 | 148.08 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998088 TOLK2 230 2 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 33.16 | 100.51 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998088 TOLK2 230 2 | 20G | System Intact | 478 |  | 31.32 | 101.35 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 62.43 | 125.63 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525531 TOLK 6 230 998089 ABBXNL844501 230 1 | 20G | System Intact | 478 |  | 75.98 | 123.2 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | 20SP, 24L, 24SP, 24WP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 956 | 40.57 | 117.64 |  |  |  | Tolk to Tuco 345kV New Line (DISIS-2017-001) | Build approximately 54 miles of new 345kV line from Tolk to Tuco
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 19WP, 24L, 24SP, 24WP, 29SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 69.86 | 194 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998079 ABBXNL844501 230 1 | 19WP, 24L, 24SP, 24WP, 29SP | System Intact | 478 |  | 76.13 | 179.04 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 20SP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | 553 | 61.02 | 171.96 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998083 ABBXNL844501 230 1 | 20SP | System Intact | 478 |  | 66.59 | 147.21 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998088 TOLK2 230 2 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 33.61 | 100.66 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998088 TOLK2 230 2 | 20G | System Intact | 478 |  | 31.75 | 101.74 |  |  |  | Tolk 345/230kV Transformer Ckt 3 (DISIS-2017-001) | Install a new 345/230kV Transformer at Tolk
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 20G | P42:345:OKGE:SB_BAER7314 |  | 553 | 61.59 | 125.5 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525549 TOLK 7 345 998089 ABBXNL844501 230 1 | 20G | System Intact | 478 |  | 74.93 | 123.37 |  |  |  | Tolk 345/230 kV CKT 2 Transformer (DISIS-2016-002) | Build new 345/230 kV Transformer Ckt 2 at Tolk to achieve a minimum emergency rating of 921 MVA on the Crossroads - Tolk 345 kV Ckt 1 line.
06ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 998077 UPDATE LATER 230 1 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 47.11 | 133.54 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 40.6 | 116.5 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 998078 SIEM 8743066 230 2 | 20G | System Intact | 559 |  | 52.06 | 107.96 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 997.3 | N/A | 109.65 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 998077 UPDATE LATER 230 1 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 45.77 | 133.6 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 20G | P12:345:SPS:J15.1.XRDS.TOLK |  | 643 | 40.13 | 118.47 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
06ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 998078 SIEM 8743066 230 2 | 20G | System Intact | 559 |  | 51.58 | 108.9 |  |  |  | Crawfish Draw 345/230kV Transformer Ckt 1 (DISIS-2017-001) | Install a new 345/230kV Transformer at Crawfish Draw
07ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
07ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
08ALL | ERIS | Non-Converge | Non-Converge | 19WP | P23:345:AEPW:RIVERSIDE CB 3413A NBTB | [7 empty] | Invalid Contingency | Contingency not valid - unit at PRWINDG1 (530690) removed with area interchange disabled.
08ALL | ERIS | Non-Converge | Non-Converge | 20SP, 24SP, 29SP | P23:345:WERE:JEC_345-16:: | [7 empty] | Invalid Contingency | Contingency not valid - large unit at JEC U2 (532652) removed with area interchange disabled.
08ALL | ERIS | Non-Converge | Non-Converge | 19WP, 24WP | P23:345:WERE:WOLF_345-50:: | [7 empty] | Invalid Contingency | Contingency not valid - large unit at WCGS U1 (532751) removed with area interchange disabled.
08ALL | ERIS | Non-Converge | Non-Converge | 19WP | P43:345:GRDA:GRDA CB9580 | [7 empty] | Invalid Contingency | Lock Shunt at NEO184B1 (547709)
08ALL | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 20SP, 24SP, 29SP | System Intact | 194 |  | 103.45 | 105.47 |  |  |  | Afton to Ketchum 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Afton to Ketchum 161kV 12.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA
08ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 20SP, 24SP, 29SP | System Intact | 194 |  | 106.71 | 108.72 |  |  |  | Pensacola to Ketchum 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Pensacole to Ketchum 161kV 4.8 mile line to achieve a minimum Summer/Emergency rating of 225 MVA
08ALL | ERIS | Thermal | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:WERE:WAVS-LACY_345:: |  | 956 | 104.26 | 131.72 |  |  |  | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA
08ALL | ERIS | Thermal | 532793 NEOSHO 7 345 588544 G17-009-TAP 345 1 | 19WP, 20G, 24WP | System Intact | 956 |  | 80.21 | 103.87 |  |  |  | Neosho to G17-009 Tap Rebuild (DISIS-2017-001) | Rebuild the existing Neosho to G17-009 345kV 18.17 mile line to achieve a minimum Winter/Emergency rating of 1260 MVA
08ALL | ERIS | Thermal | 532798 VIOLA 7 345 997930 VIOLA TX-1 138 1 | 29SP | P23:345:WERE:WICH_345-116:: |  | 440 | 94.15 | 104.06 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 532798 VIOLA 7 345 997931 VIOLA TX-1 138 1 | 24SP | P23:345:WERE:WICH_345-116:: |  | 440 | 94.02 | 104.22 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 532798 VIOLA 7 345 997935 VIOLA TX-1 138 1 | 20SP | P23:345:WERE:WICH_345-116:: |  | 440 | 94.65 | 104.81 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 532799 WAVERLY7 345 542981 LACYGNE7 345 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:161:WERE:NSES-EMDE_161:: |  | 223 | 94.91 | 128.35 |  |  |  | Franklin to G17-005 Tap 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Franklin to G17-005 Tap 161kV 20.56 mile line to achieve a minimum Winter/Emergency rating of 300 MVA
08ALL | ERIS | Thermal | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 | 19WP, 24WP | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 88.72 | 113.39 |  |  |  | Litchfield to Franklin 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Litchfield to Franklin 161kV 6.22 mile line to achieve a minimum Winter/Emergency rating of 300 MVA
08ALL | ERIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 19WP, 20G, 24WP | P12:161:WERE:NSES-EMDE_161:: | 251 |  | 105.64 | 129.13 |  |  |  | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (EMDE) | Rebuild the existing Litchfield to Asbury Plant 161kV 5.2 mile line to achieve a minimum Winter/Emergency rating of 325 MVA
08ALL | ERIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 19WP, 20G, 24WP | P12:161:WERE:NSES-EMDE_161:: | 251 |  | 105.64 | 129.13 |  |  |  | Litchfield to Asbury Plant 161kV Rebuild (DISIS-2017-001) (WERE) | Rebuild the existing Litchfield to Asbury Plant 161kV 1.6 mile line to achieve a minimum Winter/Emergency rating of 325 MVA
08ALL | ERIS | Thermal | 532937 NEOSHO 5 161 547469 RIV4525 161 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | System Intact | 205 |  |  | 174.51 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 754 MVA, no mitigation is required
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 588504 G17-005-TAP 161 1 | 19WP, 24WP, 29SP | System Intact | 220 |  | 74.69 | 108.15 |  |  |  | Franklin to G17-005 Tap 161kV Rebuild (DISIS-2017-001) | Rebuild the existing Franklin to G17-005 Tap 161kV 20.56 mile line to achieve a minimum Winter/Emergency rating of 300 MVA
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997850 FRAN TX-1 69.0 1 | 29SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 76.58 | 130.73 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997851 FRAN TX-1 69.0 1 | 24SP, 24WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 72.63 | 114.8 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997852 FRAN TX-1 69.0 1 | 19WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 71.16 | 111.76 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997855 FRAN TX-1 69.0 1 | 20SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 70.61 | 109.64 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997861 FRAN TX-1 69.0 1 | 20G | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 64.77 | 108.74 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533075 VIOLA 4 138 997930 VIOLA TX-1 138 1 | 29SP | P23:345:WERE:WICH_345-116:: |  | 440 | 93.01 | 102.4 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 533075 VIOLA 4 138 997931 VIOLA TX-1 138 1 | 24SP | P23:345:WERE:WICH_345-116:: |  | 440 | 92.94 | 102.61 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 533075 VIOLA 4 138 997935 VIOLA TX-1 138 1 | 20SP | P23:345:WERE:WICH_345-116:: |  | 440 | 93.26 | 102.86 |  |  |  | Viola 345/138kV Transformer CKT 2 (DISIS-2016-002-2) | Build second 345/138/13.8kV transformer at Viola.
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997850 FRAN TX-1 69.0 1 | 29SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 74.55 | 115.26 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997851 FRAN TX-1 69.0 1 | 24SP, 24WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 75.41 | 114.98 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997852 FRAN TX-1 69.0 1 | 19WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 69.68 | 109.22 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997855 FRAN TX-1 69.0 1 | 20SP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 69.07 | 108.24 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997861 FRAN TX-1 69.0 1 | 20G | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 63.88 | 107.6 |  |  |  | Franklin 161/69kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 161/69kV Transformer at Franklin
08ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 24WP | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 67.19 | 100.28 |  |  |  | Model Correction | 2021 ITP models show the Rate B for this line is 322 MVA, no mitigation is required
08ALL | ERIS | Thermal | 589305 G17-092XFMR2 34.5 589300 GEN-2017-092 345 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | System Intact | 125 |  |  | 103.15 |  |  |  | Interconnection Facilities | Project Equipment will be built to enure no thermal overloads on collector system, no mitigation required
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:KETCHEM-MULLINCREEK-MCREACT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:MULLINCREEK-HOLT-MULLINREACTS | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC:MINGO-SETAB::531451-531465(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1) | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P14:345:GMO-OPPD:S3458 REACTOR | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:161-345:GMO-NPPD:STJOE_R5-33::STJOE-COOPER-STJOET22 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:KCPL-GMO:NASHUA_R2-11::NASHUA-HAWTHORN-STJOE | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P23:345:SUNC:HLC_BRK282 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-CPR-3304 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Cooper Joe 345kV New Substation (DISIS-2017-001) | Build a new 345 kV substation at Cooper Joe. Tap the Cooper to St. Joe 345kV line 20 miles from St. Joe 345kV
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 6 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Cooper Joe to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 60 miles of new 345kV line from Cooper Joe to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Non-Converge | Non-Converge | 20G | P42:345:NPPD:BKR-RW-3302 | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (GMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
09ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 998123 WAUK 90343-A 230 1 | 24L | System Intact | 516 |  | 90.25 | 101.18 |  |  |  | Potter County 345/230kV Transformer Ckt 2 (DISIS-2017-001) | Install a new 345/230kV Transformer at Potter County
09ALL | ERIS | Thermal | 530592 SMOKYHL6 230 532873 SUMMIT 6 230 1 | 20G, 24L | System Intact | 319 |  | 108.36 | 115.53 |  |  |  | Smokey Hils to Summit 230kV Rebuild (DISIS-2017-001) (MIDW) | Rebuild the existing Smokey Hills to Summit 230kV 16.1 mile line to achieve a minimum Light/Emergency rating of 375 MVA
09ALL | ERIS | Thermal | 560347 DIXONCO 230 640386 TWIN CH4 230 1 | 24L | System Intact | 320 |  | 84.79 | 100.16 |  |  |  | Dixon County to Twin Church 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Dixon County to Twin Church 230kV 27.7 mile line to achieve a minimum light/emergency rating of 325 MVA
09ALL | ERIS | Thermal | 631143 OTTUMWA3 345 635730 MNTZUMA3 345 1 | 24L | System Intact | 478 |  | 99.02 | 106.42 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 956 MVA, no mitigation is required
09ALL | ERIS | Thermal | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | 20G | System Intact | 956 |  | 98.55 | 103.98 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 19WP, 20G, 20SP, 24L, 24WP, 29SP | System Intact | 926 |  | 135.06 | 144.9 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 635730 MNTZUMA3 345 635740 DIAMOND TRL3 345 1 | 20G | System Intact | 956 |  | 111.46 | 115.24 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 956 |  | 137.9 | 142.35 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 636399 HILLS-DT-RX3 345 636400 HILLS 3 345 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 956 |  | 137.65 | 142.09 |  |  |  | MISO Facilities | Facilities are not under SPP tariff
09ALL | ERIS | Thermal | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 92.28 | 141.82 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 92.28 | 141.82 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640068 B.SPRGS7 115 640091 BRULE 7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 92.28 | 141.82 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 82.44 | 127.45 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 82.44 | 127.45 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640091 BRULE 7 115 659801 OGALALA_-TS7 115 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 82.44 | 127.45 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 20G, 20SP | System Intact | 1195 |  | 95.78 | 108.34 |  |  |  | Cooper 345kV Terminal Upgrades (DISIS-2017-001) (NPPD) | Upgrade terminal equipment at Cooper 345 kV line to achieve a minimum Spring/Emergency rating of 1295 MVA
09ALL | ERIS | Thermal | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 20G, 20SP | System Intact | 1195 |  | 95.78 | 108.34 |  |  |  | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (KCPL) | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA
09ALL | ERIS | Thermal | 640138 COOPER JOE 345 640139 COOPER 3 345 1 | 20G, 20SP | System Intact | 1195 |  | 95.78 | 108.34 |  |  |  | Cooper Joe to Cooper 345kV Rebuild (DISIS-2017-001) (OPPD) | Rebuild Cooper Joe to Cooper 345 kV 22.2 miles line to achieve a minimum Spring/Emergency rating of 1295 MVA
09ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 19WP, 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 86.14 | 104.72 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 19WP, 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 86.14 | 104.72 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 19WP, 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 86.14 | 104.72 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997390 HOSKINS T2 230 1 | 29SP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 83.01 | 113.9 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997391 HOSKINS T2 230 1 | 24SP, 24WP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 85.02 | 115.62 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997393 HOSKN T4 115 1 | 19WP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 89.17 | 119.61 |  |  |  | Hoskins 345/230kV Transformer T2 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 389 MVA
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997395 HOSKINS T2 230 1 | 19WP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 79.45 | 110.67 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997396 HOSKN T4 115 1 | 20SP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 90.41 | 120.56 |  |  |  | Hoskins 345/230kV Transformer T2 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 389 MVA
09ALL | ERIS | Thermal | 640226 HOSKINS3 345 997398 HOSKINS T2 230 1 | 20SP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 80.49 | 111.66 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640227 HOSKINS4 230 997390 HOSKINS T2 230 1 | 29SP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 81.62 | 111.83 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640227 HOSKINS4 230 997391 HOSKINS T2 230 1 | 24SP, 24WP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 83.56 | 113.46 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640227 HOSKINS4 230 997395 HOSKINS T2 230 1 | 19WP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 77.89 | 108.52 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640227 HOSKINS4 230 997398 HOSKINS T2 230 1 | 20SP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 79.26 | 109.88 |  |  |  | Hoskins 345/230kV Transformer T4 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 406 MVA
09ALL | ERIS | Thermal | 640228 HOSKINS7 115 997393 HOSKN T4 115 1 | 19WP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 87.62 | 117.63 |  |  |  | Hoskins 345/230kV Transformer T2 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 389 MVA
09ALL | ERIS | Thermal | 640228 HOSKINS7 115 997396 HOSKN T4 115 1 | 20SP | P42:345:NPPD:BKR-HOS-3310 |  | 336 | 89.3 | 119 |  |  |  | Hoskins 345/230kV Transformer T2 Replacement (DISIS-2017-001) | Replace the existing Hoskins 345/230kV Transformer to achieve a minimum emergency rating of 389 MVA
09ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 116.14 | 129.8 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
09ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 116.14 | 129.8 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
09ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 116.14 | 129.8 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
10ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
10ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
12ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
12ALL | ERIS | Thermal | None |  | None | [7 empty] | None | N/A
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (TMO) | Build approximately 26 miles of new 345kV line from Holt to Hoyt
13ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:GMO-OPPD:S3458-HOLT | [7 empty] | Holt to Hoyt 345kV New Line (DISIS-2017-001) (WERE) | Build approximately 100 miles of new 345kV line from Holt to Hoyt
13ALL | ERIS | Thermal | 532772 STRANGR7 345 532775 87TH 7 345 1 | 19WP, 20G, 24WP | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN |  | 1195 | 109 | 110.75 |  |  |  | Model Correction | With the Soldier Creek WF project to convert the Stranger Creek 345kV substation to Breaker and Half configuration, the new ratings on the Stranger Creek-87th Street 345kV line for winter will be: Rate A (MVA) = 1388 and Rate B (MVA) = 1515
14ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP, 24WP | P12:345:AEPW-WFEC:VALIANT7:HUGO7 |  | 287 | 75.98 | 105.87 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (AEPW) | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA
14ALL | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 19WP, 24WP | P12:345:AEPW-WFEC:VALIANT7:HUGO7 |  | 287 | 75.98 | 105.87 |  |  |  | Valiant 138kV Terminal Upgrades (DISIS-2017-001) (WFEC) | Upgrade terminal equipment at Valiant to Hugo PP4 138kV to achieve a minimum winter/emergency rating of 305 MVA
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | [7 empty] | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | [7 empty] | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON | [7 empty] | Modify Contingency | Update contingency to remove line outage out of 659424
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | [7 empty] | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | [7 empty] | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) | [7 empty] | Modify Contingency | Update contingency to remove line outage out of 659424
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | [7 empty] | Ft. Thompson 345kV Terminal Upgrades (DISIS-2017-001) (WAPA) | Upgrade terminal equipment at Ft. Thompson 345kV to accept G16-017 Tap to Ft. Thompson Ckt 2
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | [7 empty] | G16-017 Tap to Ft. Thompson 345kV Ckt 2 (DISIS-2017-001) (BEPC) | Build approximately 30 miles of new 345kV line from G16-017 Tap to Ft. Thompson
15ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) | [7 empty] | Modify Contingency | Update contingency to remove line outage out of 659424
15ALL | ERIS | Thermal | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 20G | System Intact | 926 |  | 100.49 | 103.44 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 1083 MVA, no mitigation is required
15ALL | ERIS | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 20G, 20SP, 24L, 24SP, 29SP | P23:345:XEL:396 BKR SPK |  | 720 | 107.88 | 125.43 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 956 MVA, no mitigation is required
15ALL | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 20G, 20SP, 24L, 24SP, 29SP | P23:345:XEL:396 BKR SPK |  | 720 | 107.71 | 125.22 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 956 MVA, no mitigation is required
16ALL | ERIS | Non-Converge | None |  | None | [7 empty] | None | N/A
16ALL | ERIS | Thermal | 652468 HEBRON 4 230 661053 MANDAN 4 230 1 | 20SP, 24SP, 29SP | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1 |  | 264 | 84.53 | 113.27 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 352 MVA, no mitigation is required
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997093 BD KU2A 230 1 | 29SP | System Intact | 400 |  | 98.18 | 108.83 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997094 BD KU2A 230 1 | 24SP | System Intact | 400 |  | 102.33 | 112.41 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 997103 BD KU2A 230 1 | 20SP | System Intact | 400 |  | 99.51 | 109.59 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696) |  | 506 | 86.68 | 140.65 |  |  |  | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA
16ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696) |  | 506 | 86.68 | 140.65 |  |  |  | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997093 BD KU2A 230 1 | 29SP | System Intact | 400 |  | 101.01 | 113.27 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997094 BD KU2A 230 1 | 24SP | System Intact | 400 |  | 105.68 | 117.6 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997103 BD KU2A 230 1 | 20SP | System Intact | 400 |  | 102.51 | 114.17 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 997109 BD KU2A 230 1 | 20G | System Intact | 400 |  | 87.36 | 100.16 |  |  |  | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA
16ALL | ERIS | Thermal | 661091 NAPOLEON SW4 230 661094 WISHEK 4 230 1 | 20SP, 24SP, 29SP | System Intact | 343 |  | 99.24 | 118.58 |  |  |  | Napoleon SW to Wishek 230kV Rebuild (DISIS-2017-001) | Rebuild the existing Napoleon SW to Wishek 230kV 24.89 mile line to achieve a minimum Summer/Normal rating of 407 MVA
16ALL | ERIS | Thermal | 661093 MERRCRT4 230 661094 WISHEK 4 230 1 | 20SP, 24SP, 29SP | System Intact | 343 |  | 97.47 | 116.79 |  |  |  | MERRCRT4 to Wishek 230kV Rebuild (DISIS-2017-001) | Rebuild the existing MERRCRT4 to Wishek 230kV 29.3 mile line to achieve a minimum Summer/Normal rating of 401 MVA
17ALL | ERIS | Non-Converge | Non-Converge | 19WP, 20G, 20SP | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) | [7 empty] | New Underwood 230kV Reactive Support (DISIS-2017-001) | Install +75 MVAR Capacitor Bank(s) at New Underwood 230kV
17ALL | ERIS | Thermal | 588594 G17-014-TAP 230 659188 PHILIP_T-BE4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1 |  | 342 | 70.75 | 111.86 |  |  |  | Model Correction | 2021 ITP models show the Rate A for this line is 461 MVA, no mitigation is required
17ALL | ERIS | Thermal | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  |  | 102.18 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
17ALL | ERIS | Thermal | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  |  | 102.18 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 588595 G17-014XFMR2 34.5 588590 GEN-2017-014 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 160 |  |  | 102.18 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 73.49 | 102.46 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
17ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 73.49 | 102.46 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 73.49 | 102.46 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.39 | 121.79 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (NPPD) | Build approximately 80 miles of new 345kV line from Keystone to Sidney
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.39 | 121.79 |  |  |  | Keystone to Sidney 345kV Ckt 2 (DISIS-2017-001) (TSGT) | Review for potential impacts to TSGT facilities from Keystone to Sidney Ckt 2
17ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 93.39 | 121.79 |  |  |  | Sidney 345kV Terminal Upgrades (DISIS-2017-001) (BEPC) | Upgrade terminal equipment at Sidney 345kV to accept Keystone to Sidney Ckt 2